## Calculator
Refrigerant Charge Estimator
**Fill in Green Cells**
System Name:
Refrigerant Type: |  |  |  | Condenser | LBS
Application: |  |  |  | Configuration | of Refrigerant
Mechanical Subcooling? |  |  |  |  | #N/A
Condenser Liquid Piping (From Condenser to Rack) |  |  |  | Length (ft) (each) | LBS of Refrigerant | Confirmation | Refrigerants | Line Sizes |  | Application | Condenser Charge
[5 empty] | #N/A | YES | R-22 | 0 | 0 | Low Temp |  | Low Temp | Medium Temp | HVAC
Condenser Piping (From Rack to Condenser) |  |  |  | Length (ft) (each) | LBS of Refrigerant | NO | R-404A | 3/8" | 0.25 | Medium Temp | 1 x 2 | 47 | 44 | 20
[5 empty] | #N/A | N/A | R-134A | 1/2" | 0.375 | HVAC | 1 x 3 | 64 | 57 | 30
[7 empty] | R-402A | 5/8" | 0.5 |  | 1 x 4 | 141 | 121 | 70
Space/HW Reclaim Lines |  |  |  |  | LBS |  |  | 7/8" | 0.75 |  | 1 x 5 | 164 | 136 | 86
Location |  | Size to Reclaim | Size From Reclaim | Distance (ft) | of Refrigerant |  |  | 1-1/8" | 1 |  | 1 x 6 | 168 | 139 | 102
Reclaim Circuit #1 |  |  |  |  | #N/A |  |  | 1-3/8" | 1.25 |  | 2 x 2 | 70 | 65 | 29
Reclaim Circuit #2 |  |  |  |  | #N/A |  |  | 1-5/8" | 1.5 |  | 2 x 3 | 97 | 86 | 44
Reclaim Circuit #3 |  |  |  |  | #N/A |  |  | 2-1/8" | 2 |  | 2 x 4 | 211 | 181 | 104
[8 empty] | 2-5/8" | 2.5 |  | 2 x 5 | 245 | 202 | 125
Receiver |  |  |  |  | LBS |  |  | 3-1/8" | 3 |  | 2 x 6 | 333 | 275 | 201
Receiver Diameter (Inches) |  | Length (ft) | % Full |  | of Refrigerant |  |  | 3-5/8" | 3.5
[5 empty] | #N/A |  |  | 4-1/8" | 4
[8 empty] | 4-5/8" | 4.5
Suction Manifold |  | For multiple | Liquid Manifold |  | LBS |  |  | 6" | 5.875
Diameter | Length (ft) | Suction Headers | Diameter | Length (ft) | of Refrigerant
|  | use total length |  |  | #N/A
Fixture Piping (Loops) |  |  |  |  | LBS
Loop # | Suction Line | Length (ft) | Liquid Line | Length (ft) | of Refrigerant
1 |  |  |  |  | #N/A
2 |  |  |  |  | #N/A
3 |  |  |  |  | #N/A
4 |  |  |  |  | #N/A
5 |  |  |  |  | #N/A
6 |  |  |  |  | #N/A
7 |  |  |  |  | #N/A
8 |  |  |  |  | #N/A
9 |  |  |  |  | #N/A
10 |  |  |  |  | #N/A
11 |  |  |  |  | #N/A
12 |  |  |  |  | #N/A
13 |  |  |  |  | #N/A
14 |  |  |  |  | #N/A
15 |  |  |  |  | #N/A
16 |  |  |  |  | #N/A
17 |  |  |  |  | #N/A
18 |  |  |  |  | #N/A
19 |  |  |  |  | #N/A
20 |  |  |  |  | #N/A
Fixture Piping (Branches) |  |  |  |  | LBS
Circuit # | Suction Line | Length (ft) | Liquid Line | Length (ft) | of Refrigerant
1 |  |  |  |  | #N/A
2 |  |  |  |  | #N/A
3 |  |  |  |  | #N/A
4 |  |  |  |  | #N/A
5 |  |  |  |  | #N/A
6 |  |  |  |  | #N/A
7 |  |  |  |  | #N/A
8 |  |  |  |  | #N/A
9 |  |  |  |  | #N/A
10 |  |  |  |  | #N/A
11 |  |  |  |  | #N/A
12 |  |  |  |  | #N/A
13 |  |  |  |  | #N/A
14 |  |  |  |  | #N/A
15 |  |  |  |  | #N/A
16 |  |  |  |  | #N/A
17 |  |  |  |  | #N/A
18 |  |  |  |  | #N/A
19 |  |  |  |  | #N/A
20 |  |  |  |  | #N/A
Other (Must Provide Detailed Description and Calculation Method) |  |  |  |  | LBS of Refrigerant
|  | Total LBS of Refrigerant in System |  |  | #N/A

## Density & Volume (hidden)
Temperature | Liquid Density (lb/ft3) |  |  |  | Temperature | Vapor Density (lb/ft3)
(oF) | R-22 | R-404A | R-134A | R-402A | (oF) | R-22 | R-404A | R-134A | R-402A
-40 | 88.006 | 80.11 | 88.31 | 88.71 | -40 | 0.30342 | 0.4355 | 0.1727 | 0.4791
-35 | 87.501 | 79.57 | 87.81 | 88.08 | -35 | 0.34181 | 0.4896 | 0.1977 | 0.5383
-30 | 86.991 | 79.02 | 87.31 | 87.44 | -30 | 0.38389 | 0.5488 | 0.2254 | 0.6029
-25 | 86.476 | 78.47 | 86.81 | 86.8 | -25 | 0.42993 | 0.6135 | 0.2562 | 0.6733
-20 | 85.956 | 77.92 | 86.3 | 86.14 | -20 | 0.48018 | 0.6837 | 0.2901 | 0.7501
-15 | 85.431 | 77.37 | 85.79 | 85.48 | -15 | 0.53489 | 0.76 | 0.3276 | 0.8335
-10 | 84.901 | 76.81 | 85.28 | 84.82 | -10 | 0.59436 | 0.8429 | 0.3688 | 0.9242
-5 | 84.366 | 76.25 | 84.76 | 84.14 | -5 | 0.65887 | 0.9329 | 0.414 | 1.0226
0 | 83.825 | 75.68 | 84.23 | 83.46 | 0 | 0.72872 | 1.0304 | 0.4634 | 1.1291
5 | 83.277 | 75.11 | 83.7 | 82.78 | 5 | 0.80422 | 1.136 | 0.5174 | 1.2443
10 | 82.724 | 74.53 | 83.17 | 82.08 | 10 | 0.88571 | 1.2501 | 0.5762 | 1.3683
15 | 82.164 | 73.95 | 82.63 | 81.38 | 15 | 0.97352 | 1.3734 | 0.6402 | 1.5021
20 | 81.597 | 73.35 | 82.08 | 80.66 | 20 | 1.068 | 1.5066 | 0.7097 | 1.6464
25 | 81.023 | 72.75 | 81.52 | 79.94 | 25 | 1.1696 | 1.6502 | 0.7851 | 1.8018
30 | 80.441 | 72.13 | 80.96 | 79.22 | 30 | 1.2786 | 1.8051 | 0.8667 | 1.9693
35 | 79.852 | 71.51 | 80.4 | 78.48 | 35 | 1.3956 | 1.972 | 0.9549 | 2.1495
40 | 79.255 | 70.86 | 79.82 | 77.73 | 40 | 1.5208 | 2.1518 | 1.0501 | 2.3435
45 | 78.648 | 70.2 | 79.24 | 76.98 | 45 | 1.6549 | 2.3456 | 1.1527 | 2.5522
50 | 78.033 | 69.53 | 78.64 | 76.22 | 50 | 1.7984 | 2.5544 | 1.2633 | 2.7768
55 | 77.408 | 68.83 | 78.04 | 75.45 | 55 | 1.9517 | 2.7794 | 1.3823 | 3.0184
60 | 76.773 | 68.11 | 77.43 | 74.67 | 60 | 2.1154 | 3.0219 | 1.5102 | 3.2785
65 | 76.126 | 67.36 | 76.81 | 73.88 | 65 | 2.2903 | 3.2834 | 1.6477 | 3.5585
70 | 75.469 | 66.59 | 76.18 | 73.07 | 70 | 2.4769 | 3.5657 | 1.7952 | 3.8601
75 | 74.799 | 65.78 | 75.54 | 72.26 | 75 | 2.676 | 3.8707 | 1.9536 | 4.1852
80 | 74.115 | 64.94 | 74.89 | 71.44 | 80 | 2.8885 | 4.2005 | 2.1234 | 4.5361
85 | 73.42 | 64.05 | 74.22 | 70.6 | 85 | 3.1151 | 4.5578 | 2.3056 | 4.9152
90 | 72.708 | 63.12 | 73.54 | 69.76 | 90 | 3.357 | 4.9454 | 2.5009 | 5.3253
95 | 71.98 | 62.14 | 72.84 | 68.9 | 95 | 3.6151 | 5.3668 | 2.7102 | 5.7699
100 | 71.236 | 61.1 | 72.13 | 68.02 | 100 | 3.8907 | 5.8262 | 2.9347 | 6.2529
105 | 70.472 | 60 | 71.4 | 67.14 | 105 | 4.1852 | 6.3285 | 3.1754 | 6.7789
110 | 69.689 | 58.83 | 70.66 | 66.23 | 110 | 4.5 | 6.8797 | 3.4337 | 7.3536
115 | 68.883 | 57.57 | 69.89 | 65.31 | 115 | 4.837 | 7.4874 | 3.711 | 7.9837
120 | 68.054 | 56.22 | 69.1 | 64.36 | 120 | 5.1981 | 8.1611 | 4.0089 | 8.6779
125 | 67.197 | 54.76 | 68.29 | 63.4 | 125 | 5.5856 | 8.9132 | 4.3294 | 9.447
130 | 66.312 | 53.18 | 67.46 | 62.4 | 130 | 6.0022 | 9.7602 | 4.6745 | 10.305
135 | 65.394 | 51.43 | 66.6 | 61.37 | 135 | 6.451 | 10.7254 | 5.0468 | 11.2709
140 | 64.44 | 49.5 | 65.7 | 60.29 | 140 | 6.936 | 11.843 | 5.4491 | 12.3713
145 | 63.445 | 47.32 | 64.78 | 59.16 | 145 | 7.4615 | 13.1673 | 5.8849 | 13.6455
150 | 62.402 | 44.79 | 63.81 | 57.94 | 150 | 8.0331 | 14.7948 | 6.3584 | 15.156
200 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0