## General Notes
1. This file is a cleaned up version of my "ASHRAE RHB chapter 1 tables and charts" Excel file, a NIST RefProp linked file I'm using to generate Chapter 1
data. This file has no external links nor does it require NIST RefProp. I-P and SI versions for each figure, table and example problem are placed in
their own tab so they can be easily compared. The tabs are in the order the items appear in the chapter. This approach should simplify things for
the folks reviewing the data and doing the page layout.
One must refer to my "ASHRAE RHB chapter 1 tables and charts" and "RL Capacities" Excel files for the calculations used to generate the Chapter 1 data.
2. I've selected refrigerants 32, 290, 448A/449A,454A, 454B, 454C, 455A, 457A and 516A. I elected to use a smaller table for 290 as it will unlikely ever be
used in large capacity systems. Current refrigerants 448A and 449A will invariably be used in new equipment in 2026. 454B is the heir apparent for 410A.
454A, 454C, 455A, 457A, and 516A are the current contenders for future commercial refrigeration systems. By my polling data, 454A is the favorite despite
the fact its GWP is above 150 (237, IPCC AR5 100-year). However, EPA SNAP Rule 26 allows for it use.
Currently, I have 4 more tables than in the 2022 RHB.
It would be a simple matter for me to set up tables for any other refrigerants if someone considers them important.
3. No reference to Table 25 (Table 21 in the 2022 RHB) exists in chapter 1. A reference to it should be made in Section 8. An example problem (Example #4)
is provided in this Excel file.

## Table 1
I-P & SI
Table 1: Common and New Low-GWP Refrigerants
|  | ASHRAE | GWP 100-year2
ASHRAE No. | Type1 | 34 Safety
|  | Group | AR4 | AR5 | AR6
R-32 | HFC | A2L | 675 | 677 | 771
R-134a | HFC | A1 | 1430 | 1300 | 1530
R-290 (propane) | HC | A3 | 3.3 | --- | ---
R-404A | HFC | A1 | 3922 | 3943 | 4728
R-410A | HFC | A1 | 2088 | 1924 | 2256
R-448A | HFC/HFO | A1 | 1387 | 1273 | 1494
R-449A | HFC/HFO | A1 | 1397 | 1282 | 1504
R-450A | HFC/HFO | A1 | 604 | 547 | 643
R-454A | HFC/HFO | A2L | 239 | 238 | 270
R-454B | HFC/HFO | A2L | 466 | 467 | 531
R-454C | HFC/HFO | A2L | 148 | 146 | 166
R-455A | HFC/HFO | A2L | 148 | 146 | 166
R-457A | HFC/HFO | A2L | 139 | 139 | 159
R-507A | HFC | A2L | 3985 | 3985 | 4775
R-513A | HFC/HFO | A1 | 631 | 573 | 673
R-516A | HFC/HFO | A2L | 142 | 131 | 153
R-600a (isobutane) | HC | A3 |  | 13
R-744 (CO2) | --- | A1 | 1 | 1 | 1
R-1234yf | HFO | A2L | 44 | <1 | 0.501
R-1234ze(E) | HFO | A2L | 64 | <1 | 1.37
1HFC=hydrofluorocarbon, HFO=hydrofluoroolefin; HC=hydrocarbon.
2Intergovernmental Panel on Climate Change (IPCC) 4th, 5th and 6th assessment reports (AR4, AR5 and AR6 respectively). GWPs for R-400 and 500 series blends are calculated.
3R-600a GWP from World Meteorological Organization (WMO) 2022.
4The IPCC 4th assessment report does not explicitly list a GWP for either R-1234yf or R-1234ze(E). The U.S. EPA uses a value of 1 for each (5th assessment) in their 4th assessment calculations. Listed 4th assessment values are published by National Refrigerants.

## Page 1.2 Table (new)
I-P & SI
EPA SNAP Approval | Effective Date
|  | Application1 | ASHRAE No.
Rule 22 | Sept 7, 2018 | Domestic Refrigerators | R-290 (propane), R-441A
|  | and Freezers | R-600a (isobutane)
|  | Residential and Light | R-32, R-452B,
|  | Commercial A/C | R-454A, R-454B, R-454C,
Rule 23 | June 7, 2021 | and Heat Pump | R-457A
|  | Stand-Alone Retail | R-448A, R-449A, R-449B
Food Refrigeration
|  | Comfort Cooling | R-32, R-452B,
|  | and Industrial | R-454A, R-454B, R-454C,
Rule 25 | May 30, 2023 | Process Chillers | R-1234yf
|  | Very Low Temperature | R-1150 (ethylene)
Refrigeration
R-32,
|  | Commercial and | R-454A, R-454B, R-454C,
Rule 26 | July 15, 2024 | Industrial | R-455A, R-457A, R-516A,
|  | Refrigeration | R-290 (propane),
R-1234yf, R-1234ze(E)
1Refer to EPA SNAP publication for specific use conditions and restrictions.
European Union
F-gas Regulation (EU) 2024/573
Entered into force 11 March 2024
|  |  |  | Product Category2 | Global Warmin Potential (GWP) Limit | Date of prohibition
STATIONARY REFRIGERATION
|  |  |  | (2) Domestic refrigerators and freezers: | (a) that contain HFC's with GWP of 150 or more; | 1st January 2015
[5 empty] | (b) that contain any fluorinated greenhouse gases, except for SRE3 | 1st January 2026
|  |  |  | (3) Refrigerators and freezers for commercial use (self-contained equipment): | (a) that contain HFC's with GWP of 2500 or more; | 1st January 2020
[5 empty] | (b) that contain HFCs with GWP of 150 or more; | 1st January 2022
[5 empty] | (c) that contain other fluorinated greenhouse gases with a GWP of 150 or more. | 1st January 2025
|  |  |  | (4) Any self-contained refrigeration equipment, except chillers | that contains fluorinated greenhouse gases with a GWP of 150 or more, except for SRE3 | 1st January 2025
|  |  |  | (5) Refrigeration equipment, except chillers and equipment covered in points (4) and (6), that contains, or whose function relies upon: | (a) HFCs with a GWP of 2500 or more, except equipment intended for application designed to cool products to temperatures below -50°C; | 1st January 2020
[5 empty] | (b) fluorinated greenhouse gases with a GWP of 2500 or more, except equipment intended for application designed to cool products to temperatures below -50°C; | 1st January 2025
[5 empty] | (c) fluorinated greenhouse gases with a GWP of 150 or more, except for SRE3 | 1st January 2030
|  |  |  | (6) Multipack centralized refrigerations systems for commercial use with a rated capacity of 40kW or more that contain, or whose functioning relies upon: | fluorinated greenhouse gases with a GWP of 150 or more, except in the primary refrigerant circuit of cascade systems where fluorinated greenhouse gases with a GWP of less than 1500 may be used. | 1st January 2022
STATIONARY CHILLERS
|  |  |  | (7) Chillers that contain, or whose function relies upon: | (a) HFCs with a GWP of 2500 or more, except equipment intended for application designed to cool products to temperatures below -50°C; | 1st January 2020
[5 empty] | (b) fluorinated greenhouse gases with a GWP of 150 or more for chillers up to and including a rated capacity of 12 kW, except for SRE3 | 1st January 2027
[5 empty] | (c) fluorinated greenhouse gases for chillers up to and including a rated capacity of 12 kW, except for SRE3 | 1st January 2032
[5 empty] | (d) fluorinated greenhouse gases with a GWP up to 750 for chillers with a rated capacity above 12 kW, except for SRE3 | 1st January 2027
STATIONARY AIR-CONDITIONING EQUIPMENT AND STATIONARY HEAT PUMPS
|  |  |  | (8) Self-contained air conditioning equipment and heat pumps, except chillers, that: | (a) plug-in room air conditioning equipment which is moveable between rooms by the end user that contains HFCs with GWP of 150 or more; | 1st January 2020
[5 empty] | (b) plug-in room air-conditioning equipment, monoblock air-conditioning equipment, other self-contained air-conditioning equipment and self-contained heat pumps, with a maximum rated capacity of up to and including 12 kW that contain fluorinated greenhouse gases with a GWP of 150 or more, except if required to meet safety requirements. If safety requirements at the site of operation would not allow using fluorinated greenhouse gases with GWP of less than 150, the GWP limit is 750; | 1st January 2027
[5 empty] | (c) plug-in room air-conditioning equipment, monoblock air-conditioning equipment, other self-contained air-conditioning equipment and self-contained heat pumps, with a maximum rated capacity of up to and including 12 kW that contain fluorinated greenhouse gases, except if required to meet safety requirements. If safety requirements at the site of operation would not allow using alternatives to fluorinated greenhouse gases, the GWP limit is 750; | 1st January 2032
[5 empty] | (d) monoblock and other self-contained air-conditioning equipment and heat pumps, with a maximum rated capacity of more than 12 kW but not exceeding 50 kW that contains fluorinated greenhouse gases with a GWP of 150 or more, except if required to meet safety requirements. If safety requirements at the site of operation would not allow using fluorinated greenhouse gases with GWP of less than 150, the GWP limit is 750; | 1st January 2027
[5 empty] | (e) other self-contained air-conditioning equipment and heat pumps that contain fluorinated greenhouse gases with GWP of 150 or more, except if required to meet safety requirements. If safety requirements at the site of operation would not allow using fluorinated greenhouse gases with GWP of less than 150, the GWP limit is 750. | 1st January 2030
|  |  |  | (9) Split air-conditioning equipment and heat pumps, including fixed double duct heat pump and air-conditioning equipment: | (a) Single split systems, containing less than 3 kg of fluorinated greenhouse gases listed in Annex I, that contain, or whose functioning relies upon, fluorinated greenhouse gases listed in Annex I with GWP of 750 or more; | 1st January 2025
[5 empty] | (b) Split air-to-water systems of a rated capacity up to and including 12 kW containing, or whose functioning relies upon, fluorinated greenhouse gases with GWP of 150 or more, except if required to meet safety requirements at the site of operation; | 1st January 2027
[5 empty] | (c) Split air-to-air systems of a rated capacity up to and including 12 kW containing, or whose functioning relies upon, fluorinated greenhouse gases with GWP of 150 or more, except if required to meet safety requirements at the site of operation; | 1st January 2029
[5 empty] | (d) Split systems of a rated capacity up to and including 12 kW containing, or whose functioning relies upon, fluorinated greenhouse gases, except if required to meet safety requirements at the site of operation; | 1st January 2035
[5 empty] | (e) Split systems of a rated capacity of more than 12 kW containing, or whose functioning relies upon, fluorinated greenhouse gases with GWP of 750 or more, except if required to meet safety requirements at the site of operation; | 1st January 2029
[5 empty] | (f) Split systems of a rated capacity of more than 12 kW containing, or whose functioning relies upon, fluorinated greenhouse gases with GWP of 150 or more, except if required to meet safety requirements at the site of operation. | 1st Janurary 2033
2Refer to Official Journal of EU for (EU) 2024/573 for definitions, specific use conditions and restrictions.
3SRE is a Safety Requirement Exemption that may apply at the site of operations and exempts that specific site from the prohibition.

## Table 2
I-P
Table 2 Recommended Gas Line Velocities
Suction Line | 700 to 4000 fpm
Suction Riser | 1200 to 4000 fpm
Discharge Line | 2000 to 3500 fpm
SI
Table 2 Recommended Gas Line Velocities
Suction Line | 3.5 to 20 m/s
Suction Riser | 6.0 to 20 m/s
Discharge Line | 10 to 18 m/s

## Fig 1
I-P
Refrigerant Flow Rate, lb/min-ton
| Liquid | Evaporator Leaving Temp (Dew Point), °F
| Temp, °F | -40 | -30 | -20 | -10 | 0 | 10 | 20 | 30 | 40 | 50
| 0° | 1.7092 | 1.6918 | 1.6754 | 1.66 | 1.6458 | 1.6326 | 1.6207 | 1.6099 | 1.6005 | 1.5925
| 10° | 1.7655 | 1.7469 | 1.7295 | 1.7131 | 1.698 | 1.684 | 1.6712 | 1.6598 | 1.6498 | 1.6413
| 20° | 1.8266 | 1.8067 | 1.788 | 1.7705 | 1.7543 | 1.7394 | 1.7258 | 1.7136 | 1.7029 | 1.6939
| 30° | 1.893 | 1.8716 | 1.8516 | 1.8328 | 1.8155 | 1.7995 | 1.785 | 1.7719 | 1.7605 | 1.7508
| 40° | 1.9656 | 1.9426 | 1.921 | 1.9008 | 1.8822 | 1.865 | 1.8494 | 1.8354 | 1.8232 | 1.8127
| 50° | 2.0454 | 2.0205 | 1.9972 | 1.9754 | 1.9553 | 1.9367 | 1.9199 | 1.9048 | 1.8916 | 1.8804
| 60° | 2.1338 | 2.1067 | 2.0813 | 2.0577 | 2.0359 | 2.0158 | 1.9976 | 1.9813 | 1.967 | 1.9549
| 70° | 2.2323 | 2.2027 | 2.175 | 2.1492 | 2.1254 | 2.1035 | 2.0837 | 2.0659 | 2.0504 | 2.0373
| 80° | 2.3432 | 2.3105 | 2.2801 | 2.2518 | 2.2256 | 2.2016 | 2.1799 | 2.1605 | 2.1436 | 2.1292
| 90° | 2.4692 | 2.4329 | 2.3992 | 2.3679 | 2.339 | 2.3125 | 2.2886 | 2.2672 | 2.2485 | 2.2327
| 95° | 2.539 | 2.5007 | 2.4651 | 2.432 | 2.4015 | 2.3737 | 2.3484 | 2.3259 | 2.3063 | 2.2897
| 100° | 2.6142 | 2.5736 | 2.5359 | 2.5009 | 2.4687 | 2.4393 | 2.4126 | 2.3889 | 2.3682 | 2.3506
| 105° | 2.6955 | 2.6524 | 2.6123 | 2.5752 | 2.5411 | 2.5099 | 2.4817 | 2.4566 | 2.4347 | 2.4162
| 110° | 2.7839 | 2.7379 | 2.6952 | 2.6558 | 2.6195 | 2.5863 | 2.5564 | 2.5298 | 2.5065 | 2.4869
| 115° | 2.8804 | 2.8312 | 2.7856 | 2.7434 | 2.7047 | 2.6694 | 2.6376 | 2.6092 | 2.5845 | 2.5636
Fig 1 Flow Rate per Ton of Refrigeration for Refrigerant 454B
SI
Refrigerant Flow Rate, kg/h-kW
| Liquid | Evaporator Leaving Temp (Dew Point), °C
| Temp, °C | -40 | -35 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10
| -15° | 13.4496 | 13.3238 | 13.2047 | 13.0925 | 12.9873 | 12.8892 | 12.7985 | 12.7155 | 12.6406 | 12.5742 | 12.5171
| -10° | 13.8564 | 13.7229 | 13.5966 | 13.4777 | 13.3662 | 13.2623 | 13.1663 | 13.0785 | 12.9993 | 12.9291 | 12.8687
| -5° | 14.2942 | 14.1522 | 14.0179 | 13.8915 | 13.7731 | 13.6628 | 13.561 | 13.4678 | 13.3838 | 13.3095 | 13.2455
| 0° | 14.7671 | 14.6156 | 14.4724 | 14.3378 | 14.2116 | 14.0943 | 13.9859 | 13.8868 | 13.7975 | 13.7185 | 13.6506
| 5° | 15.2801 | 15.1179 | 14.9649 | 14.8209 | 14.6862 | 14.5609 | 14.4452 | 14.3396 | 14.2444 | 14.1602 | 14.0878
| 10° | 15.8392 | 15.6651 | 15.5008 | 15.3464 | 15.202 | 15.0677 | 14.9439 | 14.8309 | 14.7291 | 14.6391 | 14.5617
| 15° | 16.4519 | 16.264 | 16.087 | 15.9207 | 15.7654 | 15.6211 | 15.4881 | 15.3667 | 15.2574 | 15.1609 | 15.0779
| 20° | 17.127 | 16.9236 | 16.732 | 16.5522 | 16.3844 | 16.2285 | 16.085 | 15.9541 | 15.8364 | 15.7324 | 15.6431
| 25° | 17.8764 | 17.6548 | 17.4464 | 17.251 | 17.0688 | 16.8998 | 16.7442 | 16.6024 | 16.4749 | 16.3624 | 16.2658
| 30° | 18.7147 | 18.472 | 18.2439 | 18.0304 | 17.8314 | 17.647 | 17.4775 | 17.323 | 17.1843 | 17.062 | 16.9569
| 35° | 19.6615 | 19.3938 | 19.1426 | 18.9077 | 18.689 | 18.4865 | 18.3005 | 18.1313 | 17.9793 | 17.8454 | 17.7306
| 40° | 20.7434 | 20.4457 | 20.1667 | 19.9061 | 19.6639 | 19.4399 | 19.2343 | 19.0474 | 18.8798 | 18.7322 | 18.6057
| 45° | 21.9977 | 21.6632 | 21.3502 | 21.0584 | 20.7875 | 20.5373 | 20.308 | 20.0998 | 19.9132 | 19.7491 | 19.6086
Fig 1 Flow Rate per Kilowatt of Refrigeration for Refrigerant 454B
LIQUID TEMPERATURE, °F
AT EVAPORATOR FEED
LIQUID TEMPERATURE, °C
AT EVAPORATOR FEED

## Fig 2
I-P
Refrigerant Flow Rate, lb/min-ton
| Liquid | Evaporator Leaving Temp (Dew Point), °F
| Temp, °F | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 30 | 40 | 50
| 75° | 3.4438 | 3.3969 | 3.3515 | 3.3074 | 3.2647 | 3.2232 | 3.1831 | 3.1065 | 3.0346 | 2.9672
| 80° | 3.5502 | 3.5004 | 3.4522 | 3.4055 | 3.3602 | 3.3163 | 3.2738 | 3.1928 | 3.1169 | 3.0459
| 85° | 3.6645 | 3.6115 | 3.5602 | 3.5105 | 3.4624 | 3.4158 | 3.3708 | 3.285 | 3.2047 | 3.1296
| 90° | 3.7876 | 3.7309 | 3.6762 | 3.6232 | 3.572 | 3.5225 | 3.4746 | 3.3835 | 3.2984 | 3.2189
| 95° | 3.9204 | 3.8598 | 3.8012 | 3.7447 | 3.69 | 3.6371 | 3.5861 | 3.4891 | 3.3987 | 3.3144
| 100° | 4.0644 | 3.9993 | 3.9364 | 3.8758 | 3.8172 | 3.7607 | 3.7062 | 3.6027 | 3.5064 | 3.4167
| 105° | 4.221 | 4.1508 | 4.0831 | 4.0179 | 3.955 | 3.8944 | 3.8359 | 3.7252 | 3.6223 | 3.5267
| 110° | 4.392 | 4.316 | 4.2429 | 4.1726 | 4.1048 | 4.0395 | 3.9766 | 3.8578 | 3.7475 | 3.6453
| 115° | 4.5796 | 4.4971 | 4.4178 | 4.3415 | 4.2682 | 4.1977 | 4.1298 | 4.0017 | 3.8832 | 3.7736
| 120° | 4.7864 | 4.6963 | 4.6099 | 4.527 | 4.4473 | 4.3708 | 4.2973 | 4.1588 | 4.0309 | 3.9129
| 125° | 5.0158 | 4.917 | 4.8223 | 4.7316 | 4.6446 | 4.5612 | 4.4812 | 4.3308 | 4.1924 | 4.0649
Fig 2 Flow Rate per Ton of Refrigeration for Refrigerant 516A
SI
Refrigerant Flow Rate, kg/h-kW
| Liquid | Evaporator Leaving Temp (Dew Point), °C
| Temp, °C | -20 | -17.5 | -15 | -12.5 | -10 | -5 | 0 | 5 | 10 | 15 | 20
| 20° | 25.2035 | 24.9124 | 24.6289 | 24.353 | 24.0845 | 23.5687 | 23.0806 | 22.619 | 22.1831 | 21.7723 | 21.3861
| 25° | 26.5461 | 26.2233 | 25.9094 | 25.6043 | 25.3076 | 24.7387 | 24.2015 | 23.6944 | 23.2166 | 22.767 | 22.3451
| 30° | 28.0647 | 27.7042 | 27.3541 | 27.0142 | 26.6841 | 26.0525 | 25.4573 | 24.8969 | 24.3699 | 23.875 | 23.4114
| 35° | 29.7976 | 29.3915 | 28.9978 | 28.6161 | 28.246 | 27.5392 | 26.8751 | 26.2513 | 25.666 | 25.1177 | 24.6051
| 40° | 31.7955 | 31.3335 | 30.8865 | 30.4538 | 30.035 | 29.2371 | 28.4896 | 27.7896 | 27.1346 | 26.5225 | 25.9516
| 45° | 34.1271 | 33.5955 | 33.0821 | 32.5862 | 32.1071 | 31.197 | 30.3475 | 29.5544 | 28.8147 | 28.1254 | 27.4843
| 50° | 36.8885 | 36.2682 | 35.6706 | 35.0947 | 34.5396 | 33.4887 | 32.5117 | 31.6032 | 30.7588 | 29.9746 | 29.2475
Fig 2 Flow Rate per Kilowatt of Refrigeration for Refrigerant 516A
LIQUID TEMPERATURE, °F
AT EVAPORATOR FEED
LIQUID TEMPERATURE, °C
AT EVAPORATOR FEED

## Table 3
I-P
Table 3 Approximate Effect of Gas Line Pressure Drops on R-454B Compressor Capacity and Powera
Line Loss, °F | Capacity, % | Energy, %b
Suction Line
0 | 100 | 100
2 | 96.3 | 103.5
4 | 92.7 | 107.3
Discharge Line
0 | 100 | 100
2 | 99.1 | 103
4 | 98.2 | 106.1
aFor a system operating at a 40°F dew point evaporator temperature and 100°F dew point condensing temperature.
bEnergy usage as a percentage required to maintain zero line loss capacity.
SI
Table 3 Approximate Effect of Gas Line Pressure Drops on R-454B Compressor Capacity and Powera
Line Loss, K | Capacity, % | Energy, %b
Suction Line
0 | 100 | 100
1 | 96.7 | 103.2
2 | 93.5 | 106.5
Discharge Line
0 | 100 | 100
1 | 99.2 | 102.7
2 | 98.4 | 105.5
aFor a system operating at a 5°C dew point evaporator temperature and 38°C dew point condensing temperature.
bEnergy usage as a percentage required to maintain zero line loss capacity.

## Example 1
I-P
Example 1. An R-454B air conditioning system using copper pipe operates at
40°F evaporator and 105°F condensing. Capacity is 5 tons, and the
liquid line is 100 ft equivalent length with a riser of 20 ft. Determine the
liquid line size and total required subcooling.
Solution: From Table 4, the rating for the 1/2" OD liquid line at 1°F drop is 5.58 tons.
Use the equation in Note 3 of Table 4 to compute actual temperature difference. At 5 tons,
Actual temperature drop | = | 1.0(5.0/5.58)1.8 | = | 0.82°F
R-454B saturation pressure at 105°F condensing
(see R-454B properties in Chapter 29, 2025 ASHRAE
Handbook—Fundamentals) |  |  | = | 337.5 psia
R-454B saturation pressure at 104°F condensing |  |  | = | 333.0 psia
Estimated friction loss | = | 0.82(337.5 - 333.0) | = | 3.7 psi
Loss for riser | = | 20 x 0.51 | = | 10 psi
Total pressure loss | = |  |  | 13.7 psi
Initial pressure at beginning of liquid line |  |  |  | 337.5 psia
Total liquid line losses |  |  |  | -13.7 psi
Net pressure at expansion device |  |  | = | 323.8 psia
The saturation temperature at 323.8 psia is 101.9°F
Required subcooling |  |  | = | (105-101.9)
or 3.1°F
1Approximate loss in psi per foot riser for halocarbon refrigerants. For hydrocarbon refrigerants, use 0.25
SI
Example 1. An R-454B air conditioning system using copper pipe operates at
5°C evaporator and 40°C condensing. Capacity is 14 kW, and the
liquid line is 30 m equivalent length with a riser of 6 m. Determine the
liquid line size and total required subcooling.
Solution: From Table 4, the rating for the 13 mm OD liquid line at 0.5 K drop is 18.7 kW.
Use the equation in Note 3 of Table 4 to compute actual temperature difference. At 14 kW,
Actual temperature drop | = | 1.0(14/18.7)1.8 | = | 0.59 K
R-454B saturation pressure at 40°C condensing
(see R-454B properties in Chapter 29, 2025 ASHRAE
Handbook—Fundamentals) |  |  | = | 2296 kPa
R-454B saturation pressure at 39°C condensing |  |  | = | 2241 kPa
Estimated friction loss | = | 0.59(2296 - 2241) | = | 32 kPa
Loss for riser | = | 6 x 111 | = | 66 kPa
Total pressure loss | = |  |  | 98 kPa
Initial pressure at beginning of liquid line |  |  |  | 2296 kPa
Total liquid line losses |  |  |  | -98 kPa
Net pressure at expansion device |  |  | = | 2198 kPa
The saturation temperature at 2198 kPa is 38.2°C
Required subcooling |  |  | = | (40-38.2)
or 1.8 K
1Approximate loss in kPa per meter riser for halocarbon refrigerants. For hydrocarbon refrigerants, use 5.5

## Page 1.4 Table
I-P
Line Size | Tons, Refrigeration1
Type L, | Refrigerant
Copper, | 32 | 448A/ 449A | 454A/ 457A | 454B | 454C/ 455A
OD, in
1 1/8 | 17.3 | 11.5 | 11.1 | 14.1 | 10.3
1 3/8 | 29.3 | 19.5 | 18.8 | 23.9 | 17.4
1 5/8 | 45.2 | 30.1 | 29.1 | 36.9 | 26.9
2 1/8 | 90.2 | 60.2 | 58.1 | 73.7 | 53.7
2 5/8 | 155 | 103 | 99.8 | 127 | 92.3
3 1/8 | 242 | 161 | 156 | 198 | 144
3 5/8 | 353 | 236 | 227 | 288 | 210
4 1/8 | 490 | 327 | 315 | 400 | 292
1Capacities based on 105°F liquid temperature entering the expension device and a 40°F evaporator temperature. A flow coefficient of 0.75 is used to account for the vena contracta.
SI
Line Size | Kilowatts, Refrigeration1
Type L, | Refrigerant
Copper, | 32 | 448A/ 449A | 454A/ 457A | 454B | 454C/ 455A
OD, in (mm)
1 1/8 (29) | 61.3 | 41 | 39.6 | 50.2 | 36.6
1 3/8 (35) | 104 | 69.5 | 67 | 84.9 | 62
1 5/8 (41) | 160 | 107 | 103 | 131 | 95.7
2 1/8 (54) | 320 | 214 | 207 | 262 | 191
2 5/8 (67) | 550 | 368 | 355 | 450 | 329
3 1/8 (79) | 858 | 574 | 554 | 702 | 513
3 5/8 (92) | 1250 | 838 | 808 | 1020 | 748
4 1/8 (105) | 1740 | 1160 | 1120 | 1420 | 1040
1Capacities based on 40°C liquid temperature entering the expension device and a 5°C evaporator temperature. A flow coefficient of 0.75 is used to account for the vena contracta.

## Table 4
I-P
Table 4 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454B (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 4.41 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 4.49 psi,
Type L, |  | 1.1413 | 1.6613 | 2.3229 | 3.1412 | 4.1312 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | 0.117 | 0.181 | 0.27 | 0.387 | 0.459 | 0.591 | 1.11 | 1.23 | 2.05 | 2.27
1/2 |  | 0.178 | 0.289 | 0.448 | 0.664 | 0.952 | 1.13 | 1.45 | 2.19 | 2.42 | 5.04 | 5.58
5/8 |  | 0.324 | 0.525 | 0.812 | 1.2 | 1.72 | 2.04 | 2.62 | 3.42 | 3.78 | 9.13 | 10.1
3/4 |  | 0.553 | 0.897 | 1.38 | 2.05 | 2.93 | 3.48 | 4.45 | 5.1 | 5.65 | 15.3 | 17
7/8 |  | 0.858 | 1.39 | 2.14 | 3.16 | 4.52 | 5.37 | 6.88 | 7.09 | 7.85 | 21.3 | 23.6
1 1/8 |  | 1.75 | 2.82 | 4.34 | 6.4 | 9.13 | 10.9 | 13.9 | 12.1 | 13.4 | 36.3 | 40.2
1 3/8 |  | 3.05 | 4.93 | 7.57 | 11.1 | 15.9 | 18.9 | 24.1 | 18.4 | 20.4 | 55.2 | 61.2
1 5/8 |  | 4.68 | 7.61 | 11.8 | 17.6 | 25.1 | 29.9 | 38.1 | 26.1 | 28.9 | 78.2 | 86.6
2 1/8 |  | 8.14 | 13.2 | 20.6 | 30.9 | 45.1 | 61.8 | 78.7 | 45.3 | 50.2 | 136 | 151
2 5/8 |  | 12.6 | 20.4 | 31.8 | 47.7 | 69.6 | 105 | 139 | 69.9 | 77.4 | 210 | 232
3 1/8 |  | 17.9 | 29.1 | 45.3 | 68.1 | 99.3 | 149 | 212 | 100 | 110 | 299 | 331
3 5/8 |  | 24.2 | 39.4 | 61.3 | 92.1 | 134 | 202 | 287 | 135 | 149 | 405 | 448
4 1/8 |  | 31.5 | 51.2 | 79.7 | 120 | 175 | 263 | 373 | 175 | 194 | 526 | 583
Steel
IPS | SCH
3/8 | 80 | 0.137 | 0.217 | 0.328 | 0.476 | 0.668 | 0.803 | 1.01 | 2.06 | 2.28 | 3.62 | 4
1/2 | 80 | 0.272 | 0.429 | 0.647 | 0.937 | 1.32 | 1.58 | 1.99 | 3.43 | 3.8 | 7.12 | 7.89
3/4 | 80 | 0.614 | 0.969 | 1.46 | 2.11 | 2.96 | 3.56 | 4.48 | 6.34 | 7.01 | 16.1 | 17.8
1 | 80 | 1.21 | 1.9 | 2.86 | 4.14 | 5.8 | 6.97 | 8.77 | 10.5 | 11.7 | 31.4 | 34.8
1 1/4 | 80 | 2.59 | 4.08 | 6.13 | 8.86 | 12.4 | 14.9 | 18.8 | 18.8 | 20.8 | 56.4 | 62.4
1 1/2 | 80 | 3.96 | 6.22 | 9.34 | 13.5 | 18.9 | 22.8 | 28.6 | 25.9 | 28.7 | 77.7 | 86
2 | 40 | 8.83 | 14.3 | 21.7 | 31.4 | 43.9 | 52.9 | 66.4 | 49.2 | 54.4 | 147 | 163
2 1/2 | 40 | 12.6 | 20.5 | 31.9 | 47.9 | 69.8 | 84.2 | 106 | 70.1 | 77.7 | 210 | 233
3 | 40 | 19.5 | 31.6 | 49.2 | 73.9 | 108 | 149 | 187 | 108 | 120 | 325 | 360
4 | 40 | 33.5 | 54.4 | 84.7 | 127 | 186 | 279 | 380 | 187 | 206 | 560 | 619
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.22 | 1.14 | 1.05 | 0.95 | 0.86 | 0.77 | 0.67
| Suction Line |  | 1.14 | 1.09 | 1.03 | 0.97 | 0.91 | 0.84 | 0.77
| Discharge Line |  | 0.85 | 0.91 | 0.97 | 1.03 | 1.07 | 1.11 | 1.13
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 4 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454B (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 27.1 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 27.6 kPa,
Type L, |  | 7.096 | 9.966 | 13.5403 | 20.3718 | 26.006 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | 0.241 | 0.376 | 0.561 | 0.962 | 1.33 | 1.53 | 1.97 | 3.89 | 4.31 | 6.87 | 7.6
1/2 (13) |  | 0.599 | 0.931 | 1.39 | 2.37 | 3.26 | 3.76 | 4.85 | 7.64 | 8.46 | 16.9 | 18.7
5/8 (16) |  | 1.09 | 1.69 | 2.52 | 4.29 | 5.9 | 6.81 | 8.76 | 11.9 | 13.2 | 30.6 | 33.9
3/4 (19) |  | 1.87 | 2.89 | 4.29 | 7.3 | 10 | 11.6 | 14.9 | 17.8 | 19.7 | 52.2 | 57.8
7/8 (22) |  | 2.89 | 4.48 | 6.64 | 11.3 | 15.5 | 17.9 | 23 | 24.8 | 27.4 | 74.3 | 82.3
1 1/8 (29) |  | 5.89 | 9.09 | 13.5 | 22.8 | 31.3 | 36.2 | 46.4 | 42.2 | 46.8 | 127 | 140
1 3/8 (35) |  | 10.3 | 15.9 | 23.5 | 39.8 | 54.5 | 63.1 | 80.7 | 64.3 | 71.2 | 193 | 214
1 5/8 (41) |  | 16.3 | 25.1 | 37.2 | 62.8 | 86 | 100 | 127 | 91.1 | 101 | 273 | 303
2 1/8 (54) |  | 28.4 | 44 | 65.8 | 114 | 160 | 206 | 263 | 158 | 175 | 475 | 526
2 5/8 (67) |  | 43.7 | 67.8 | 102 | 176 | 247 | 360 | 464 | 244 | 271 | 733 | 812
3 1/8 (79) |  | 62.4 | 96.8 | 145 | 251 | 352 | 514 | 733 | 349 | 386 | 1050 | 1160
3 5/8 (92) |  | 84.4 | 131 | 196 | 340 | 476 | 696 | 992 | 472 | 522 | 1410 | 1570
4 1/8 (105) |  | 110 | 170 | 255 | 442 | 619 | 904 | 1290 | 613 | 679 | 1840 | 2040
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.465 | 0.704 | 1.03 | 1.7 | 2.3 | 2.68 | 3.39 | 7.19 | 7.97 | 12.2 | 13.5
1/2 (13) | 80 | 0.919 | 1.39 | 2.02 | 3.34 | 4.52 | 5.29 | 6.67 | 12 | 13.3 | 24 | 26.6
3/4 (19) | 80 | 2.08 | 3.14 | 4.56 | 7.53 | 10.2 | 11.9 | 15 | 22.1 | 24.5 | 54.1 | 59.9
1 (25) | 80 | 4.08 | 6.16 | 8.94 | 14.7 | 19.9 | 23.3 | 29.4 | 36.8 | 40.8 | 106 | 117
1 1/4 (32) | 80 | 8.77 | 13.2 | 19.2 | 31.6 | 42.7 | 50 | 62.9 | 65.7 | 72.7 | 197 | 218
1 1/2 (38) | 80 | 13.4 | 20.2 | 29.2 | 48.2 | 65.1 | 76.2 | 95.9 | 90.5 | 100 | 271 | 301
2 (51) | 40 | 30.8 | 46.9 | 67.9 | 112 | 151 | 177 | 223 | 172 | 190 | 515 | 571
2 1/2 (64) | 40 | 43.9 | 68 | 102 | 177 | 241 | 282 | 355 | 245 | 271 | 735 | 814
3 (76) | 40 | 67.8 | 105 | 157 | 273 | 382 | 498 | 626 | 378 | 419 | 1140 | 1260
4 (102) | 40 | 117 | 181 | 271 | 470 | 658 | 961 | 1270 | 652 | 722 | 1960 | 2170
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.24 | 1.16 | 1.08 | 0.92 | 0.84 | 0.75 | 0.66
| Suction Line |  | 1.15 | 1.1 | 1.05 | 0.95 | 0.89 | 0.83 | 0.77
| Discharge Line |  | 0.83 | 0.89 | 0.95 | 1.05 | 1.09 | 1.12 | 1.14
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 5
I-P
Table 5 Suction, Discharge, and Liquid Line Capacities for Refrigerant 290 (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 2.56 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 2.56 psi,
Type L, |  | 0.75957 | 1.0822 | 1.4841 | 1.9708 | 2.5471 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
1/4 |  | 0.0331 | 0.054 | 0.0839 | 0.125 | 0.18 | 0.204 | 0.271 | 0.271 | 0.334 | 0.812 | 1
5/16 |  | 0.0683 | 0.111 | 0.172 | 0.256 | 0.367 | 0.417 | 0.554 | 0.463 | 0.571 | 1.39 | 1.71
3/8 |  | 0.123 | 0.199 | 0.31 | 0.465 | 0.666 | 0.756 | 1 | 0.726 | 0.895 | 2.18 | 2.68
1/2 |  | 0.241 | 0.392 | 0.609 | 0.914 | 1.33 | 1.85 | 2.45 | 1.43 | 1.76 | 4.28 | 5.28
5/8 |  | 0.377 | 0.612 | 0.952 | 1.43 | 2.08 | 3.27 | 4.41 | 2.23 | 2.75 | 6.68 | 8.24
3/4 |  | 0.563 | 0.914 | 1.42 | 2.13 | 3.11 | 4.89 | 6.85 | 3.33 | 4.1 | 10 | 12.3
7/8 |  | 0.783 | 1.27 | 1.97 | 2.96 | 4.32 | 6.79 | 9.52 | 4.62 | 5.7 | 13.9 | 17.1
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 20 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 20 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.22 | 1.13 | 1.04 | 0.96 | 0.87 | 0.78 | 0.7
| Suction Line |  | 1.16 | 1.1 | 1.03 | 0.97 | 0.9 | 0.83 | 0.76
| Discharge Line |  | 0.85 | 0.91 | 0.97 | 1.03 | 1.08 | 1.12 | 1.14
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 5 Suction, Discharge, and Liquid Line Capacities for Refrigerant 290 (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 15.7 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 15.7 kPa,
Type L, |  | 4.7221 | 6.5046 | 8.6823 | 12.7463 | 16.0189 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
1/4 (6) |  | 0.124 | 0.193 | 0.288 | 0.492 | 0.68 | 0.751 | 1 | 0.946 | 1.17 | 2.84 | 3.5
5/16 (8) |  | 0.255 | 0.396 | 0.59 | 1.01 | 1.39 | 1.53 | 2.04 | 1.62 | 2 | 4.86 | 5.99
3/8 (10) |  | 0.428 | 0.663 | 0.991 | 1.72 | 2.4 | 2.78 | 3.7 | 2.54 | 3.13 | 7.61 | 9.39
1/2 (13) |  | 0.842 | 1.3 | 1.95 | 3.38 | 4.72 | 6.8 | 9.03 | 4.98 | 6.15 | 14.9 | 18.5
5/8 (16) |  | 1.32 | 2.04 | 3.04 | 5.27 | 7.38 | 11.3 | 15.8 | 7.79 | 9.61 | 23.4 | 28.8
3/4 (19) |  | 1.96 | 3.04 | 4.55 | 7.87 | 11 | 16.8 | 23.6 | 11.6 | 14.4 | 34.9 | 43.1
7/8 (22) |  | 2.73 | 4.22 | 6.32 | 10.9 | 15.3 | 23.4 | 32.8 | 16.2 | 19.9 | 48.5 | 59.8
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 5 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 5 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.23 | 1.15 | 1.08 | 0.92 | 0.84 | 0.77 | 0.69
| Suction Line |  | 1.17 | 1.11 | 1.06 | 0.94 | 0.88 | 0.82 | 0.75
| Discharge Line |  | 0.83 | 0.89 | 0.95 | 1.05 | 1.09 | 1.12 | 1.15
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 6
I-P
Table 6 Suction, Discharge, and Liquid Line Capacities for Refrigerants 448A/449A (Intermediate- or Low-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesb |  | Liquid Linesb
Line Size |  | corresponding Dp, psi)a |  |  |  |  | (Dt = 1°F, Dp = 0.85 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 0.98 psi,
Type L, |  | 0.21631 | 0.29013 | 0.49199 | 0.78022 | 0.96182 | max velocity 3000 fpm)a |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -90 | -80 | -60 | -40 | -30 | -90 | -30 | -90 | -30 | -90 | -30
3/8 |  | --- | --- | --- | --- | --- | --- | 0.111 | 1.65 | 1.83 | 1 | 1.11
1/2 |  | --- | --- | --- | 0.156 | 0.204 | 0.221 | 0.275 | 3.24 | 3.59 | 2.51 | 2.78
5/8 |  | --- | --- | 0.158 | 0.284 | 0.371 | 0.403 | 0.501 | 5.06 | 5.61 | 4.59 | 5.08
3/4 |  | --- | 0.139 | 0.27 | 0.486 | 0.635 | 0.69 | 0.857 | 7.56 | 8.38 | 7.86 | 8.71
7/8 |  | 0.149 | 0.216 | 0.421 | 0.755 | 0.985 | 1.07 | 1.33 | 10.5 | 11.6 | 12.2 | 13.5
1 1/8 |  | 0.307 | 0.443 | 0.86 | 1.54 | 2.01 | 2.18 | 2.7 | 17.9 | 19.8 | 25 | 27.7
1 3/8 |  | 0.541 | 0.78 | 1.51 | 2.69 | 3.51 | 3.82 | 4.73 | 27.3 | 30.2 | 43.8 | 48.5
1 5/8 |  | 0.863 | 1.24 | 2.4 | 4.27 | 5.56 | 6.06 | 7.5 | 38.6 | 42.8 | 69.5 | 77
2 1/8 |  | 1.73 | 2.46 | 4.68 | 8.3 | 10.8 | 12.6 | 15.6 | 67.2 | 74.4 | 145 | 161
2 5/8 |  | 2.67 | 3.79 | 7.21 | 12.8 | 16.7 | 22.4 | 27.6 | 104 | 115 | 258 | 285
3 1/8 |  | 3.81 | 5.41 | 10.3 | 18.3 | 23.8 | 35.8 | 44.1 | 148 | 164 | 412 | 457
3 5/8 |  | 5.15 | 7.32 | 13.9 | 24.7 | 32.2 | 49.8 | 65.7 | 200 | 222 | 600 | 665
4 1/8 |  | 6.69 | 9.52 | 18.1 | 32.1 | 41.9 | 64.7 | 85.4 | 260 | 288 | 780 | 864
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 0°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -60°F evaporator temperature, and are suitable in the range of -90°F to -30°F.
Condensing Temperature, °F
|  |  | -30 | -20 | -10 | 0 | 10 | 20 | 30
| Liquid Line |  | 1.16 | 1.11 | 1.05 | 1 | 0.95 | 0.89 | 0.84
| Suction Line |  | 1.11 | 1.08 | 1.04 | 1 | 0.96 | 0.92 | 0.88
| Discharge Line |  | 0.63 | 0.74 | 0.86 | 1 | 1.15 | 1.3 | 1.47
aSee section on Pressure Drop Considerations.
bSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 6 Suction, Discharge, and Liquid Line Capacities for Refrigerants 448A/449A (Intermediate- or Low-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesb |  | Liquid Linesb
Line Size |  | corresponding Dp, kPa)a |  |  |  |  | (Dt = 0.5 K, Dp = 5.72 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 6.61 kPa,
Type L, |  | 1.1899 | 2.0186 | 3.2138 | 4.8519 | 7.0058 | max velocity 15 m/s)a |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -70 | -60 | -50 | -40 | -30 | -70 | -30 | -70 | -30 | -70 | -30
3/8 (10) |  | --- | --- | 0.12 | 0.205 | 0.331 | 0.315 | 0.41 | 5.51 | 6.24 | 3.42 | 3.87
1/2 (13) |  | --- | 0.166 | 0.301 | 0.512 | 0.823 | 0.785 | 1.02 | 10.8 | 12.3 | 8.54 | 9.67
5/8 (16) |  | 0.156 | 0.305 | 0.551 | 0.933 | 1.5 | 1.43 | 1.85 | 16.9 | 19.2 | 15.6 | 17.7
3/4 (19) |  | 0.269 | 0.524 | 0.945 | 1.6 | 2.56 | 2.45 | 3.17 | 25.3 | 28.6 | 26.7 | 30.3
7/8 (22) |  | 0.42 | 0.817 | 1.47 | 2.48 | 3.97 | 3.8 | 4.92 | 35.1 | 39.8 | 41.5 | 47.1
1 1/8 (29) |  | 0.864 | 1.67 | 3.01 | 5.06 | 8.07 | 7.74 | 10 | 59.8 | 67.8 | 84.8 | 96.1
1 3/8 (35) |  | 1.52 | 2.94 | 5.27 | 8.86 | 14.1 | 13.6 | 17.5 | 91.1 | 103 | 149 | 168
1 5/8 (41) |  | 2.43 | 4.69 | 8.38 | 14.1 | 22.4 | 21.5 | 27.7 | 129 | 146 | 236 | 268
2 1/8 (54) |  | 5.06 | 9.55 | 16.9 | 28.2 | 45 | 44.8 | 57.6 | 224 | 254 | 493 | 558
2 5/8 (67) |  | 7.8 | 14.7 | 26 | 43.5 | 69.4 | 79.4 | 102 | 346 | 392 | 874 | 991
3 1/8 (79) |  | 11.1 | 21 | 37.1 | 62.1 | 99.1 | 127 | 163 | 494 | 560 | 1400 | 1590
3 5/8 (92) |  | 15.1 | 28.4 | 50.2 | 83.9 | 134 | 181 | 243 | 668 | 757 | 2000 | 2270
4 1/8 (105) |  | 19.6 | 36.9 | 65.3 | 109 | 174 | 235 | 327 | 868 | 984 | 2610 | 2950
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on -15°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -50°C evaporator temperature, and are suitable in the range of -70°C to -30°C.
Condensing Temperature, °C
|  |  | -30 | -25 | -20 | -15 | -10 | -5 | 0
| Liquid Line |  | 1.15 | 1.1 | 1.05 | 1 | 0.95 | 0.9 | 0.85
| Suction Line |  | 1.11 | 1.07 | 1.04 | 1 | 0.96 | 0.93 | 0.89
| Discharge Line |  | 0.66 | 0.77 | 0.88 | 1 | 1.13 | 1.26 | 1.4
aSee section on Pressure Drop Considerations.
bSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 7
I-P
Table 7 Suction, Discharge, and Liquid Line Capacities for Refrigerants 448A/449A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 3.44 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 3.61 psi,
Type L, |  | 0.78022 | 1.1709 | 1.679 | 2.3181 | 3.1018 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | --- | 0.101 | 0.158 | 0.236 | 0.308 | 0.412 | 0.834 | 1.01 | 1.27 | 1.53
1/2 |  | --- | 0.154 | 0.25 | 0.389 | 0.58 | 0.757 | 1.01 | 1.64 | 1.98 | 3.13 | 3.78
5/8 |  | 0.162 | 0.28 | 0.455 | 0.704 | 1.05 | 1.37 | 1.83 | 2.56 | 3.09 | 5.67 | 6.85
3/4 |  | 0.278 | 0.478 | 0.776 | 1.2 | 1.78 | 2.33 | 3.1 | 3.82 | 4.61 | 9.67 | 11.7
7/8 |  | 0.431 | 0.741 | 1.2 | 1.86 | 2.76 | 3.59 | 4.79 | 5.31 | 6.41 | 15 | 18.1
1 1/8 |  | 0.879 | 1.51 | 2.44 | 3.76 | 5.57 | 7.27 | 9.67 | 9.05 | 10.9 | 27.2 | 32.8
1 3/8 |  | 1.54 | 2.63 | 4.25 | 6.55 | 9.7 | 12.6 | 16.8 | 13.8 | 16.6 | 41.4 | 49.9
1 5/8 |  | 2.44 | 4.17 | 6.73 | 10.4 | 15.3 | 20 | 26.5 | 19.5 | 23.6 | 58.6 | 70.7
2 1/8 |  | 4.74 | 8.13 | 13.3 | 20.8 | 31.4 | 41.3 | 54.8 | 34 | 41 | 102 | 123
2 5/8 |  | 7.32 | 12.5 | 20.5 | 32 | 48.4 | 72.7 | 96.5 | 52.4 | 63.2 | 157 | 190
3 1/8 |  | 10.4 | 17.9 | 29.2 | 45.7 | 69.1 | 116 | 154 | 74.7 | 90.2 | 224 | 271
3 5/8 |  | 14.1 | 24.2 | 39.5 | 61.8 | 93.5 | 171 | 228 | 101 | 122 | 303 | 366
4 1/8 |  | 18.4 | 31.5 | 51.3 | 80.4 | 122 | 222 | 318 | 131 | 159 | 394 | 476
Steel
IPS | SCH
3/8 | 80 | --- | 0.117 | 0.186 | 0.282 | 0.411 | 0.534 | 0.704 | 1.54 | 1.86 | 2.29 | 2.76
1/2 | 80 | 0.139 | 0.232 | 0.367 | 0.556 | 0.81 | 1.05 | 1.39 | 2.57 | 3.1 | 4.5 | 5.44
3/4 | 80 | 0.314 | 0.524 | 0.829 | 1.25 | 1.82 | 2.37 | 3.12 | 4.75 | 5.73 | 10.2 | 12.3
1 | 80 | 0.618 | 1.03 | 1.62 | 2.45 | 3.57 | 4.64 | 6.11 | 7.89 | 9.53 | 19.9 | 24
1 1/4 | 80 | 1.33 | 2.21 | 3.49 | 5.26 | 7.66 | 9.93 | 13.1 | 14.1 | 17 | 42.2 | 51
1 1/2 | 80 | 2.03 | 3.37 | 5.32 | 8.02 | 11.7 | 15.1 | 19.9 | 19.4 | 23.4 | 58.2 | 70.2
2 | 40 | 4.73 | 7.84 | 12.4 | 18.6 | 27.1 | 35.1 | 46.3 | 36.8 | 44.5 | 110 | 133
2 1/2 | 40 | 7.34 | 12.5 | 19.7 | 29.7 | 43.2 | 56 | 73.7 | 52.5 | 63.4 | 158 | 190
3 | 40 | 11.3 | 19.4 | 31.7 | 49.6 | 75 | 98.9 | 130 | 81.1 | 97.9 | 243 | 294
4 | 40 | 19.5 | 33.5 | 54.6 | 85.4 | 129 | 201 | 265 | 140 | 169 | 419 | 506
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.25 | 1.15 | 1.05 | 0.95 | 0.85 | 0.75 | 0.64
| Suction Line |  | 1.17 | 1.11 | 1.04 | 0.96 | 0.89 | 0.81 | 0.73
| Discharge Line |  | 0.85 | 0.91 | 0.97 | 1.03 | 1.07 | 1.09 | 1.11
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 7 Suction, Discharge, and Liquid Line Capacities for Refrigerants 448A/449A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 21.2 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 22.2 kPa,
Type L, |  | 4.8519 | 7.0058 | 9.7424 | 15.0773 | 19.543 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | 0.121 | 0.198 | 0.311 | 0.566 | 0.81 | 1.03 | 1.37 | 2.92 | 3.52 | 4.26 | 5.14
1/2 (13) |  | 0.3 | 0.493 | 0.77 | 1.4 | 1.99 | 2.52 | 3.38 | 5.73 | 6.92 | 10.5 | 12.7
5/8 (16) |  | 0.548 | 0.896 | 1.4 | 2.53 | 3.61 | 4.56 | 6.1 | 8.96 | 10.8 | 19.1 | 23
3/4 (19) |  | 0.938 | 1.53 | 2.39 | 4.31 | 6.14 | 7.76 | 10.4 | 13.4 | 16.2 | 32.5 | 39.3
7/8 (22) |  | 1.46 | 2.38 | 3.7 | 6.66 | 9.48 | 12 | 16 | 18.6 | 22.4 | 50.3 | 60.7
1 1/8 (29) |  | 2.97 | 4.83 | 7.5 | 13.5 | 19.2 | 24.3 | 32.3 | 31.7 | 38.3 | 95.1 | 115
1 3/8 (35) |  | 5.2 | 8.45 | 13.1 | 23.5 | 33.4 | 42.2 | 56.2 | 48.3 | 58.3 | 145 | 175
1 5/8 (41) |  | 8.25 | 13.4 | 20.7 | 37.2 | 52.7 | 66.6 | 88.7 | 68.3 | 82.5 | 205 | 247
2 1/8 (54) |  | 16.6 | 26.9 | 42.1 | 77 | 109 | 138 | 183 | 119 | 144 | 356 | 431
2 5/8 (67) |  | 25.5 | 41.6 | 64.9 | 119 | 172 | 243 | 323 | 183 | 221 | 550 | 664
3 1/8 (79) |  | 36.4 | 59.3 | 92.7 | 170 | 246 | 387 | 514 | 262 | 316 | 785 | 948
3 5/8 (92) |  | 49.3 | 80.2 | 125 | 230 | 332 | 574 | 763 | 354 | 427 | 1060 | 1280
4 1/8 (105) |  | 64.1 | 104 | 163 | 299 | 432 | 765 | 1070 | 460 | 555 | 1380 | 1670
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.237 | 0.379 | 0.577 | 1.01 | 1.42 | 1.79 | 2.36 | 5.4 | 6.52 | 7.71 | 9.31
1/2 (13) | 80 | 0.47 | 0.749 | 1.14 | 2 | 2.79 | 3.52 | 4.65 | 8.99 | 10.9 | 15.2 | 18.4
3/4 (19) | 80 | 1.06 | 1.69 | 2.57 | 4.5 | 6.29 | 7.93 | 10.5 | 16.6 | 20.1 | 34.3 | 41.4
1 (25) | 80 | 2.09 | 3.32 | 5.04 | 8.81 | 12.3 | 15.5 | 20.5 | 27.6 | 33.4 | 67.2 | 81.1
1 1/4 (32) | 80 | 4.5 | 7.14 | 10.8 | 18.9 | 26.4 | 33.3 | 43.9 | 49.3 | 59.5 | 144 | 174
1 1/2 (38) | 80 | 6.88 | 10.9 | 16.5 | 28.8 | 40.2 | 50.7 | 66.9 | 67.9 | 82 | 204 | 246
2 (51) | 40 | 16 | 25.3 | 38.4 | 66.9 | 93.4 | 118 | 155 | 129 | 156 | 387 | 467
2 1/2 (64) | 40 | 25.6 | 40.4 | 61.2 | 107 | 149 | 187 | 247 | 184 | 222 | 552 | 666
3 (76) | 40 | 39.5 | 64.4 | 101 | 184 | 263 | 331 | 437 | 284 | 343 | 852 | 1030
4 (102) | 40 | 68.1 | 111 | 173 | 317 | 459 | 674 | 889 | 489 | 590 | 1470 | 1770
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.27 | 1.18 | 1.09 | 0.91 | 0.82 | 0.73 | 0.64
| Suction Line |  | 1.19 | 1.13 | 1.06 | 0.93 | 0.87 | 0.8 | 0.72
| Discharge Line |  | 0.85 | 0.91 | 0.96 | 1.04 | 1.07 | 1.08 | 1.09
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 8
I-P
Table 8 Suction, Discharge, and Liquid Line Capacities for Refrigerant 32 (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 4.89 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 4.89 psi,
Type L, |  | 1.8513 | 2.1997 | 2.5897 | 3.5026 | 4.6063 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -20 | -10 | 0 | 20 | 40 | -20 | 40 | -20 | 40 | -20 | 40
3/8 |  | 0.154 | 0.192 | 0.236 | 0.348 | 0.495 | 0.599 | 0.717 | 1.45 | 1.51 | 2.83 | 2.94
1/2 |  | 0.381 | 0.474 | 0.584 | 0.858 | 1.22 | 1.47 | 1.76 | 2.85 | 2.96 | 6.96 | 7.24
5/8 |  | 0.691 | 0.86 | 1.06 | 1.55 | 2.2 | 2.67 | 3.18 | 4.45 | 4.63 | 12.6 | 13.1
3/4 |  | 1.18 | 1.47 | 1.8 | 2.64 | 3.74 | 4.54 | 5.41 | 6.65 | 6.91 | 19.9 | 20.7
7/8 |  | 1.83 | 2.27 | 2.79 | 4.08 | 5.77 | 7.01 | 8.35 | 9.23 | 9.61 | 27.7 | 28.8
1 1/8 |  | 3.71 | 4.61 | 5.66 | 8.27 | 11.7 | 14.2 | 16.9 | 15.7 | 16.4 | 47.2 | 49.1
1 3/8 |  | 6.45 | 8.04 | 9.86 | 14.4 | 20.3 | 24.7 | 29.3 | 24 | 24.9 | 71.9 | 74.8
1 5/8 |  | 9.12 | 11.4 | 14.1 | 20.9 | 30.3 | 39 | 46.3 | 33.9 | 35.3 | 102 | 106
2 1/8 |  | 15.9 | 19.8 | 24.5 | 36.4 | 52.7 | 78.5 | 95.6 | 59 | 61.4 | 177 | 184
2 5/8 |  | 24.5 | 30.5 | 37.7 | 56.2 | 81.2 | 121 | 159 | 91 | 94.7 | 273 | 284
3 1/8 |  | 34.9 | 43.6 | 53.9 | 80.2 | 116 | 173 | 227 | 130 | 135 | 390 | 406
3 5/8 |  | 47.3 | 59 | 72.9 | 108 | 157 | 234 | 306 | 176 | 183 | 527 | 549
4 1/8 |  | 61.4 | 76.6 | 94.7 | 141 | 204 | 304 | 398 | 228 | 238 | 685 | 713
Steel
IPS | SCH
3/8 | 80 | 0.286 | 0.351 | 0.427 | 0.614 | 0.854 | 1.05 | 1.23 | 2.68 | 2.79 | 4.98 | 5.18
1/2 | 80 | 0.564 | 0.693 | 0.842 | 1.21 | 1.68 | 2.07 | 2.42 | 4.47 | 4.65 | 9.81 | 10.2
3/4 | 80 | 1.27 | 1.56 | 1.9 | 2.72 | 3.78 | 4.66 | 5.45 | 8.25 | 8.58 | 22.1 | 23
1 | 80 | 2.5 | 3.06 | 3.72 | 5.33 | 7.41 | 9.12 | 10.7 | 13.7 | 14.3 | 41.2 | 42.8
1 1/4 | 80 | 5.36 | 6.57 | 7.98 | 11.4 | 15.9 | 19.5 | 22.9 | 24.5 | 25.5 | 73.4 | 76.4
1 1/2 | 80 | 8.18 | 10 | 12.2 | 17.4 | 24.2 | 29.8 | 34.8 | 33.7 | 35.1 | 101 | 105
2 | 40 | 17.2 | 21.5 | 26.5 | 39.5 | 56.1 | 69.1 | 80.9 | 64 | 66.6 | 192 | 200
2 1/2 | 40 | 24.6 | 30.6 | 37.9 | 56.4 | 81.5 | 110 | 129 | 91.3 | 95 | 274 | 285
3 | 40 | 37.9 | 47.3 | 58.5 | 87 | 126 | 188 | 228 | 141 | 147 | 423 | 440
4 | 40 | 65.3 | 81.5 | 101 | 150 | 217 | 323 | 423 | 243 | 253 | 729 | 758
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 10°F evaporator temperature, and are suitable in the range of -20°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.2 | 1.12 | 1.04 | 0.96 | 0.88 | 0.79 | 0.7
| Suction Line |  | 1.12 | 1.07 | 1.02 | 0.97 | 0.92 | 0.87 | 0.81
| Discharge Line |  | 0.84 | 0.9 | 0.97 | 1.03 | 1.09 | 1.14 | 1.19
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 8 Suction, Discharge, and Liquid Line Capacities for Refrigerant 32 (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 30.1 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 30.1 kPa,
Type L, |  | 11.1054 | 15.0941 | 19.945 | 22.7163 | 28.9962 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -30 | -20 | -10 | -5 | 5 | -30 | 5 | -30 | 5 | -30 | 5
3/8 (10) |  | 0.494 | 0.733 | 1.05 | 1.24 | 1.7 | 1.98 | 2.39 | 5.05 | 5.26 | 9.45 | 9.85
1/2 (13) |  | 1.23 | 1.81 | 2.58 | 3.05 | 4.17 | 4.88 | 5.88 | 9.92 | 10.3 | 23.3 | 24.3
5/8 (16) |  | 2.23 | 3.29 | 4.68 | 5.52 | 7.54 | 8.82 | 10.6 | 15.5 | 16.2 | 42.2 | 44
3/4 (19) |  | 3.8 | 5.6 | 7.97 | 9.4 | 12.8 | 15 | 18.1 | 23.1 | 24.1 | 69.4 | 72.4
7/8 (22) |  | 5.89 | 8.67 | 12.3 | 14.5 | 19.8 | 23.2 | 27.9 | 32.2 | 33.5 | 96.5 | 101
1 1/8 (29) |  | 12 | 17.6 | 25 | 29.4 | 40 | 47 | 56.3 | 54.8 | 57.2 | 164 | 172
1 3/8 (35) |  | 20.9 | 30.7 | 43.5 | 51.2 | 69.6 | 81.8 | 98 | 83.5 | 87.1 | 251 | 261
1 5/8 (41) |  | 30.3 | 45 | 64.9 | 77.1 | 107 | 129 | 155 | 118 | 123 | 355 | 370
2 1/8 (54) |  | 52.8 | 78.3 | 113 | 134 | 186 | 267 | 320 | 206 | 214 | 617 | 643
2 5/8 (67) |  | 81.4 | 121 | 174 | 207 | 288 | 412 | 548 | 317 | 331 | 951 | 992
3 1/8 (79) |  | 116 | 172 | 248 | 295 | 410 | 589 | 782 | 453 | 472 | 1360 | 1420
3 5/8 (92) |  | 157 | 233 | 336 | 399 | 555 | 796 | 1060 | 612 | 638 | 1840 | 1910
4 1/8 (105) |  | 204 | 303 | 437 | 519 | 722 | 1030 | 1380 | 796 | 830 | 2390 | 2490
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.925 | 1.34 | 1.87 | 2.18 | 2.93 | 3.49 | 4.12 | 9.34 | 9.74 | 16.7 | 17.4
1/2 (13) | 80 | 1.83 | 2.63 | 3.68 | 4.3 | 5.77 | 6.87 | 8.11 | 15.6 | 16.2 | 33 | 34.4
3/4 (19) | 80 | 4.13 | 5.94 | 8.29 | 9.69 | 13 | 15.5 | 18.3 | 28.7 | 30 | 74.3 | 77.4
1 (25) | 80 | 8.09 | 11.6 | 16.2 | 19 | 25.4 | 30.3 | 35.8 | 47.8 | 49.8 | 143 | 150
1 1/4 (32) | 80 | 17.4 | 25 | 34.8 | 40.7 | 54.5 | 64.9 | 76.6 | 85.2 | 88.9 | 256 | 267
1 1/2 (38) | 80 | 26.5 | 38.1 | 53.1 | 62 | 83 | 99 | 117 | 117 | 122 | 352 | 367
2 (51) | 40 | 57.2 | 84.9 | 122 | 144 | 193 | 230 | 271 | 223 | 232 | 669 | 697
2 1/2 (64) | 40 | 81.6 | 121 | 175 | 208 | 288 | 366 | 432 | 318 | 332 | 954 | 995
3 (76) | 40 | 126 | 187 | 270 | 320 | 445 | 639 | 762 | 491 | 512 | 1470 | 1540
4 (102) | 40 | 217 | 322 | 464 | 552 | 767 | 1100 | 1460 | 845 | 882 | 2540 | 2650
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -12°C evaporator temperature, and are suitable in the range of -30°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.21 | 1.15 | 1.07 | 0.93 | 0.85 | 0.78 | 0.7
| Suction Line |  | 1.13 | 1.09 | 1.04 | 0.95 | 0.91 | 0.86 | 0.8
| Discharge Line |  | 0.82 | 0.89 | 0.94 | 1.06 | 1.11 | 1.15 | 1.19
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 9
I-P
Table 9 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 3.53 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 3.74 psi,
Type L, |  | 0.83974 | 1.2446 | 1.7667 | 2.4196 | 3.217 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | --- | 0.11 | 0.169 | 0.25 | 0.322 | 0.43 | 0.815 | 0.978 | 1.32 | 1.59
1/2 |  | 0.1 | 0.169 | 0.271 | 0.416 | 0.614 | 0.793 | 1.06 | 1.6 | 1.92 | 3.26 | 3.92
5/8 |  | 0.181 | 0.307 | 0.492 | 0.754 | 1.11 | 1.43 | 1.91 | 2.5 | 3 | 5.91 | 7.1
3/4 |  | 0.311 | 0.525 | 0.839 | 1.28 | 1.89 | 2.44 | 3.24 | 3.74 | 4.48 | 10.1 | 12.1
7/8 |  | 0.482 | 0.813 | 1.3 | 1.98 | 2.92 | 3.77 | 5.01 | 5.19 | 6.23 | 15.6 | 18.7
1 1/8 |  | 0.982 | 1.65 | 2.64 | 4.02 | 5.9 | 7.61 | 10.1 | 8.85 | 10.6 | 26.6 | 31.9
1 3/8 |  | 1.72 | 2.89 | 4.6 | 7 | 10.3 | 13.2 | 17.6 | 13.5 | 16.2 | 40.4 | 48.5
1 5/8 |  | 2.73 | 4.57 | 7.28 | 11.1 | 16.2 | 20.9 | 27.7 | 19.1 | 22.9 | 57.2 | 68.7
2 1/8 |  | 5.13 | 8.66 | 13.9 | 21.6 | 32.4 | 43.2 | 57.3 | 33.2 | 39.8 | 100 | 119
2 5/8 |  | 7.91 | 13.4 | 21.5 | 33.3 | 49.9 | 76.2 | 101 | 51.2 | 61.4 | 154 | 184
3 1/8 |  | 11.3 | 19.1 | 30.7 | 47.5 | 71.2 | 121 | 161 | 73.1 | 87.7 | 219 | 263
3 5/8 |  | 15.3 | 25.8 | 41.5 | 64.3 | 96.4 | 174 | 238 | 98.8 | 119 | 296 | 356
4 1/8 |  | 19.9 | 33.5 | 54 | 83.6 | 125 | 226 | 324 | 128 | 154 | 385 | 462
Steel
IPS | SCH
3/8 | 80 | --- | 0.128 | 0.201 | 0.301 | 0.435 | 0.56 | 0.736 | 1.51 | 1.81 | 2.36 | 2.84
1/2 | 80 | 0.154 | 0.254 | 0.396 | 0.593 | 0.857 | 1.1 | 1.45 | 2.51 | 3.01 | 4.66 | 5.59
3/4 | 80 | 0.349 | 0.573 | 0.894 | 1.34 | 1.93 | 2.48 | 3.26 | 4.64 | 5.57 | 10.5 | 12.6
1 | 80 | 0.686 | 1.12 | 1.75 | 2.62 | 3.78 | 4.86 | 6.39 | 7.72 | 9.26 | 20.6 | 24.7
1 1/4 | 80 | 1.47 | 2.41 | 3.76 | 5.61 | 8.1 | 10.4 | 13.7 | 13.8 | 16.5 | 41.3 | 49.5
1 1/2 | 80 | 2.25 | 3.68 | 5.73 | 8.56 | 12.3 | 15.9 | 20.8 | 19 | 22.7 | 56.9 | 68.2
2 | 40 | 5.24 | 8.56 | 13.3 | 19.9 | 28.6 | 36.8 | 48.4 | 36 | 43.2 | 108 | 130
2 1/2 | 40 | 7.94 | 13.4 | 21.2 | 31.7 | 45.7 | 58.7 | 77.1 | 51.4 | 61.6 | 154 | 185
3 | 40 | 12.3 | 20.7 | 33.3 | 51.6 | 77.3 | 104 | 136 | 79.3 | 95.1 | 238 | 285
4 | 40 | 21.1 | 35.6 | 57.4 | 88.8 | 133 | 211 | 277 | 137 | 164 | 410 | 492
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.25 | 1.15 | 1.05 | 0.95 | 0.85 | 0.74 | 0.64
| Suction Line |  | 1.17 | 1.11 | 1.04 | 0.96 | 0.89 | 0.81 | 0.73
| Discharge Line |  | 0.87 | 0.92 | 0.98 | 1.02 | 1.05 | 1.07 | 1.08
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 9 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 21.7 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 23.0 kPa,
Type L, |  | 5.2216 | 7.4547 | 10.2702 | 15.7202 | 20.2626 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | 0.135 | 0.218 | 0.338 | 0.605 | 0.858 | 1.07 | 1.44 | 2.85 | 3.42 | 4.45 | 5.34
1/2 (13) |  | 0.336 | 0.542 | 0.836 | 1.49 | 2.11 | 2.64 | 3.53 | 5.6 | 6.73 | 11 | 13.2
5/8 (16) |  | 0.613 | 0.986 | 1.52 | 2.7 | 3.82 | 4.78 | 6.38 | 8.76 | 10.5 | 19.9 | 23.9
3/4 (19) |  | 1.05 | 1.69 | 2.59 | 4.6 | 6.5 | 8.13 | 10.8 | 13.1 | 15.7 | 33.9 | 40.7
7/8 (22) |  | 1.63 | 2.61 | 4.01 | 7.12 | 10 | 12.6 | 16.7 | 18.2 | 21.8 | 52.4 | 62.9
1 1/8 (29) |  | 3.32 | 5.31 | 8.14 | 14.4 | 20.3 | 25.4 | 33.8 | 31 | 37.2 | 92.9 | 112
1 3/8 (35) |  | 5.81 | 9.29 | 14.2 | 25.1 | 35.3 | 44.2 | 58.8 | 47.2 | 56.6 | 142 | 170
1 5/8 (41) |  | 9.21 | 14.7 | 22.5 | 39.7 | 55.8 | 69.8 | 92.8 | 66.8 | 80.2 | 200 | 240
2 1/8 (54) |  | 17.9 | 28.7 | 44.4 | 80.1 | 115 | 144 | 192 | 116 | 139 | 349 | 418
2 5/8 (67) |  | 27.6 | 44.3 | 68.4 | 124 | 177 | 255 | 338 | 179 | 215 | 537 | 645
3 1/8 (79) |  | 39.4 | 63.2 | 97.6 | 176 | 253 | 406 | 538 | 256 | 307 | 767 | 921
3 5/8 (92) |  | 53.3 | 85.5 | 132 | 239 | 342 | 599 | 797 | 346 | 415 | 1040 | 1250
4 1/8 (105) |  | 69.3 | 111 | 172 | 310 | 445 | 779 | 1120 | 450 | 540 | 1350 | 1620
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.264 | 0.415 | 0.624 | 1.08 | 1.5 | 1.87 | 2.47 | 5.28 | 6.33 | 7.98 | 9.58
1/2 (13) | 80 | 0.522 | 0.819 | 1.23 | 2.13 | 2.95 | 3.69 | 4.86 | 8.79 | 10.5 | 15.7 | 18.9
3/4 (19) | 80 | 1.18 | 1.85 | 2.78 | 4.79 | 6.65 | 8.31 | 10.9 | 16.2 | 19.5 | 35.5 | 42.6
1 (25) | 80 | 2.32 | 3.63 | 5.45 | 9.39 | 13 | 16.3 | 21.4 | 27 | 32.4 | 69.5 | 83.4
1 1/4 (32) | 80 | 5 | 7.81 | 11.7 | 20.1 | 27.9 | 34.9 | 45.9 | 48.2 | 57.8 | 144 | 173
1 1/2 (38) | 80 | 7.63 | 11.9 | 17.8 | 30.7 | 42.5 | 53.2 | 69.9 | 66.3 | 79.6 | 199 | 239
2 (51) | 40 | 17.8 | 27.7 | 41.5 | 71.3 | 98.7 | 123 | 162 | 126 | 151 | 378 | 454
2 1/2 (64) | 40 | 27.7 | 44.2 | 66.1 | 114 | 157 | 197 | 258 | 180 | 216 | 539 | 647
3 (76) | 40 | 42.8 | 68.6 | 106 | 191 | 275 | 347 | 457 | 278 | 333 | 833 | 999
4 (102) | 40 | 73.6 | 118 | 182 | 330 | 473 | 707 | 929 | 478 | 574 | 1430 | 1720
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.27 | 1.18 | 1.09 | 0.91 | 0.82 | 0.73 | 0.63
| Suction Line |  | 1.19 | 1.13 | 1.06 | 0.93 | 0.87 | 0.8 | 0.72
| Discharge Line |  | 0.85 | 0.91 | 0.96 | 1.03 | 1.06 | 1.07 | 1.08
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 10
I-P
Table 10 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454C (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 3.02 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 3.28 psi,
Type L, |  | 0.69004 | 1.0309 | 1.4737 | 2.0308 | 2.7146 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | --- | --- | 0.13 | 0.195 | 0.261 | 0.357 | 0.714 | 0.898 | 1.06 | 1.33
1/2 |  | --- | 0.126 | 0.205 | 0.321 | 0.481 | 0.641 | 0.876 | 1.4 | 1.76 | 2.62 | 3.29
5/8 |  | 0.132 | 0.228 | 0.373 | 0.581 | 0.87 | 1.16 | 1.58 | 2.19 | 2.76 | 4.74 | 5.96
3/4 |  | 0.226 | 0.39 | 0.636 | 0.99 | 1.48 | 1.97 | 2.69 | 3.28 | 4.12 | 8.08 | 10.2
7/8 |  | 0.352 | 0.605 | 0.986 | 1.53 | 2.29 | 3.04 | 4.15 | 4.55 | 5.72 | 12.5 | 15.7
1 1/8 |  | 0.717 | 1.23 | 2 | 3.1 | 4.63 | 6.15 | 8.39 | 7.76 | 9.75 | 23.3 | 29.2
1 3/8 |  | 1.26 | 2.15 | 3.49 | 5.41 | 8.06 | 10.7 | 14.6 | 11.8 | 14.8 | 35.5 | 44.5
1 5/8 |  | 1.99 | 3.41 | 5.53 | 8.55 | 12.7 | 16.9 | 23 | 16.7 | 21 | 50.2 | 63.1
2 1/8 |  | 3.99 | 6.85 | 11.2 | 17.6 | 26.3 | 34.9 | 47.6 | 29.1 | 36.6 | 87.3 | 110
2 5/8 |  | 6.15 | 10.6 | 17.3 | 27.2 | 41.2 | 61.6 | 83.8 | 44.9 | 56.4 | 135 | 169
3 1/8 |  | 8.77 | 15.1 | 24.7 | 38.8 | 58.9 | 98.1 | 133 | 64.1 | 80.5 | 192 | 241
3 5/8 |  | 11.9 | 20.4 | 33.4 | 52.4 | 79.6 | 146 | 198 | 86.6 | 109 | 260 | 327
4 1/8 |  | 15.4 | 26.5 | 43.4 | 68.1 | 104 | 203 | 278 | 113 | 142 | 338 | 425
Steel
IPS | SCH
3/8 | 80 | --- | --- | 0.153 | 0.234 | 0.343 | 0.453 | 0.612 | 1.32 | 1.66 | 1.91 | 2.4
1/2 | 80 | 0.113 | 0.19 | 0.303 | 0.461 | 0.676 | 0.891 | 1.21 | 2.2 | 2.77 | 3.77 | 4.73
3/4 | 80 | 0.257 | 0.43 | 0.683 | 1.04 | 1.52 | 2.01 | 2.71 | 4.07 | 5.11 | 8.49 | 10.7
1 | 80 | 0.505 | 0.844 | 1.34 | 2.04 | 2.98 | 3.93 | 5.31 | 6.76 | 8.5 | 16.6 | 20.9
1 1/4 | 80 | 1.09 | 1.81 | 2.88 | 4.37 | 6.39 | 8.42 | 11.4 | 12.1 | 15.2 | 35.7 | 44.8
1 1/2 | 80 | 1.66 | 2.77 | 4.38 | 6.65 | 9.74 | 12.8 | 17.3 | 16.6 | 20.9 | 49.9 | 62.6
2 | 40 | 3.86 | 6.44 | 10.2 | 15.5 | 22.6 | 29.8 | 40.2 | 31.6 | 39.6 | 94.7 | 119
2 1/2 | 40 | 6.17 | 10.3 | 16.2 | 24.6 | 36 | 47.5 | 64.1 | 45 | 56.6 | 135 | 170
3 | 40 | 9.52 | 16.4 | 26.8 | 42.1 | 63.7 | 83.8 | 113 | 69.5 | 87.3 | 209 | 262
4 | 40 | 16.4 | 28.2 | 46.1 | 72.4 | 110 | 171 | 230 | 120 | 150 | 359 | 451
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.26 | 1.16 | 1.05 | 0.95 | 0.84 | 0.74 | 0.63
| Suction Line |  | 1.19 | 1.11 | 1.04 | 0.96 | 0.88 | 0.8 | 0.71
| Discharge Line |  | 0.87 | 0.92 | 0.98 | 1.02 | 1.06 | 1.07 | 1.08
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 10 Suction, Discharge, and Liquid Line Capacities for Refrigerant 454C (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 18.5 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 20.1 kPa,
Type L, |  | 4.291 | 6.1699 | 8.5553 | 13.2059 | 17.1028 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | --- | 0.162 | 0.255 | 0.467 | 0.672 | 0.869 | 1.19 | 2.5 | 3.14 | 3.56 | 4.48
1/2 (13) |  | 0.245 | 0.402 | 0.631 | 1.15 | 1.65 | 2.14 | 2.93 | 4.92 | 6.18 | 8.8 | 11.1
5/8 (16) |  | 0.447 | 0.732 | 1.15 | 2.09 | 2.99 | 3.87 | 5.29 | 7.68 | 9.66 | 15.9 | 20
3/4 (19) |  | 0.765 | 1.25 | 1.96 | 3.56 | 5.1 | 6.58 | 9 | 11.5 | 14.4 | 27.2 | 34.2
7/8 (22) |  | 1.19 | 1.94 | 3.03 | 5.51 | 7.88 | 10.2 | 13.9 | 15.9 | 20 | 42.1 | 52.9
1 1/8 (29) |  | 2.42 | 3.95 | 6.16 | 11.2 | 15.9 | 20.6 | 28.1 | 27.2 | 34.2 | 81.5 | 102
1 3/8 (35) |  | 4.24 | 6.91 | 10.8 | 19.5 | 27.8 | 35.8 | 48.8 | 41.4 | 52 | 124 | 156
1 5/8 (41) |  | 6.73 | 11 | 17 | 30.8 | 43.8 | 56.5 | 77 | 58.6 | 73.6 | 176 | 221
2 1/8 (54) |  | 13.9 | 22.7 | 35.4 | 63.7 | 90.7 | 117 | 159 | 102 | 128 | 306 | 384
2 5/8 (67) |  | 21.5 | 35 | 54.8 | 101 | 147 | 206 | 281 | 157 | 198 | 471 | 593
3 1/8 (79) |  | 30.6 | 50 | 78.3 | 144 | 209 | 328 | 447 | 224 | 282 | 673 | 846
3 5/8 (92) |  | 41.4 | 67.6 | 106 | 195 | 283 | 487 | 662 | 303 | 381 | 910 | 1140
4 1/8 (105) |  | 53.9 | 87.8 | 138 | 253 | 368 | 686 | 933 | 394 | 496 | 1180 | 1490
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.194 | 0.311 | 0.475 | 0.841 | 1.18 | 1.52 | 2.05 | 4.63 | 5.82 | 6.45 | 8.11
1/2 (13) | 80 | 0.384 | 0.614 | 0.938 | 1.66 | 2.33 | 2.99 | 4.04 | 7.71 | 9.69 | 12.7 | 16
3/4 (19) | 80 | 0.87 | 1.39 | 2.12 | 3.74 | 5.25 | 6.73 | 9.1 | 14.2 | 17.9 | 28.7 | 36.1
1 (25) | 80 | 1.71 | 2.73 | 4.16 | 7.32 | 10.3 | 13.2 | 17.8 | 23.7 | 29.8 | 56.2 | 70.7
1 1/4 (32) | 80 | 3.68 | 5.86 | 8.92 | 15.7 | 22.1 | 28.2 | 38.2 | 42.2 | 53.1 | 121 | 152
1 1/2 (38) | 80 | 5.63 | 8.94 | 13.6 | 23.9 | 33.6 | 43 | 58.2 | 58.2 | 73.1 | 175 | 219
2 (51) | 40 | 13.1 | 20.8 | 31.6 | 55.6 | 78 | 100 | 135 | 110 | 139 | 331 | 417
2 1/2 (64) | 40 | 20.9 | 33.2 | 50.4 | 88.6 | 124 | 159 | 215 | 158 | 198 | 473 | 595
3 (76) | 40 | 33.2 | 54.2 | 84.9 | 156 | 220 | 281 | 380 | 243 | 306 | 730 | 918
4 (102) | 40 | 57.2 | 93.4 | 146 | 269 | 391 | 572 | 773 | 419 | 527 | 1260 | 1580
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.28 | 1.19 | 1.09 | 0.91 | 0.81 | 0.72 | 0.62
| Suction Line |  | 1.2 | 1.14 | 1.07 | 0.93 | 0.86 | 0.78 | 0.7
| Discharge Line |  | 0.86 | 0.91 | 0.96 | 1.03 | 1.05 | 1.07 | 1.08
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 11
I-P
Table 11 Suction, Discharge, and Liquid Line Capacities for Refrigerant 455A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 3.22 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 3.55 psi,
Type L, |  | 0.73702 | 1.1003 | 1.572 | 2.1657 | 2.8947 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | --- | --- | 0.139 | 0.209 | 0.287 | 0.392 | 0.725 | 0.905 | 1.13 | 1.42
1/2 |  | --- | 0.135 | 0.221 | 0.344 | 0.514 | 0.705 | 0.963 | 1.42 | 1.78 | 2.8 | 3.49
5/8 |  | 0.143 | 0.246 | 0.401 | 0.622 | 0.93 | 1.28 | 1.74 | 2.23 | 2.78 | 5.07 | 6.33
3/4 |  | 0.244 | 0.42 | 0.683 | 1.06 | 1.58 | 2.17 | 2.96 | 3.32 | 4.15 | 8.63 | 10.8
7/8 |  | 0.38 | 0.652 | 1.06 | 1.64 | 2.45 | 3.35 | 4.56 | 4.62 | 5.77 | 13.4 | 16.7
1 1/8 |  | 0.774 | 1.33 | 2.15 | 3.32 | 4.95 | 6.77 | 9.21 | 7.88 | 9.83 | 23.6 | 29.5
1 3/8 |  | 1.35 | 2.32 | 3.75 | 5.79 | 8.61 | 11.8 | 16 | 12 | 15 | 36 | 44.9
1 5/8 |  | 2.15 | 3.67 | 5.93 | 9.16 | 13.6 | 18.6 | 25.3 | 17 | 21.2 | 50.9 | 63.6
2 1/8 |  | 4.21 | 7.22 | 11.8 | 18.5 | 28 | 38.4 | 52.2 | 29.5 | 36.9 | 88.6 | 111
2 5/8 |  | 6.49 | 11.1 | 18.2 | 28.5 | 43.1 | 67.8 | 92 | 45.5 | 56.9 | 137 | 171
3 1/8 |  | 9.27 | 15.9 | 25.9 | 40.6 | 61.6 | 108 | 146 | 65 | 81.1 | 195 | 243
3 5/8 |  | 12.5 | 21.5 | 35.1 | 55 | 83.3 | 160 | 217 | 87.9 | 110 | 264 | 329
4 1/8 |  | 16.3 | 27.9 | 45.6 | 71.4 | 108 | 223 | 306 | 114 | 143 | 343 | 428
Steel
IPS | SCH
3/8 | 80 | --- | 0.103 | 0.164 | 0.25 | 0.366 | 0.497 | 0.671 | 1.34 | 1.67 | 2.03 | 2.54
1/2 | 80 | 0.122 | 0.204 | 0.324 | 0.493 | 0.721 | 0.979 | 1.32 | 2.23 | 2.79 | 4.01 | 5
3/4 | 80 | 0.277 | 0.462 | 0.732 | 1.11 | 1.62 | 2.2 | 2.97 | 4.13 | 5.15 | 9.03 | 11.3
1 | 80 | 0.544 | 0.907 | 1.44 | 2.18 | 3.18 | 4.32 | 5.82 | 6.86 | 8.57 | 17.7 | 22.1
1 1/4 | 80 | 1.17 | 1.95 | 3.08 | 4.66 | 6.82 | 9.25 | 12.5 | 12.2 | 15.3 | 36.7 | 45.8
1 1/2 | 80 | 1.79 | 2.97 | 4.7 | 7.11 | 10.4 | 14.1 | 19 | 16.9 | 21.1 | 50.6 | 63.2
2 | 40 | 4.16 | 6.91 | 10.9 | 16.5 | 24.1 | 32.7 | 44.1 | 32 | 40 | 96.1 | 120
2 1/2 | 40 | 6.51 | 11 | 17.4 | 26.3 | 38.4 | 52.1 | 70.3 | 45.7 | 57 | 137 | 171
3 | 40 | 10.1 | 17.2 | 28.1 | 44.1 | 66.8 | 92 | 124 | 70.6 | 88.1 | 212 | 264
4 | 40 | 17.3 | 29.7 | 48.4 | 15.9 | 115 | 187 | 253 | 121 | 152 | 364 | 455
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.27 | 1.16 | 1.05 | 0.95 | 0.84 | 0.73 | 0.63
| Suction Line |  | 1.19 | 1.11 | 1.04 | 0.96 | 0.88 | 0.8 | 0.71
| Discharge Line |  | 0.87 | 0.93 | 0.98 | 1.02 | 1.05 | 1.06 | 1.06
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 11 Suction, Discharge, and Liquid Line Capacities for Refrigerant 455A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 19.8 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 21.9 kPa,
Type L, |  | 4.5831 | 6.5856 | 9.1272 | 14.0824 | 18.2372 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | 0.106 | 0.175 | 0.274 | 0.5 | 0.718 | 0.957 | 1.31 | 2.54 | 3.17 | 3.81 | 4.76
1/2 (13) |  | 0.265 | 0.434 | 0.678 | 1.23 | 1.77 | 2.35 | 3.22 | 4.99 | 6.23 | 9.41 | 11.8
5/8 (16) |  | 0.482 | 0.789 | 1.23 | 2.24 | 3.2 | 4.26 | 5.82 | 7.8 | 9.74 | 17.1 | 21.3
3/4 (19) |  | 0.826 | 1.35 | 2.1 | 3.81 | 5.45 | 7.24 | 9.89 | 11.6 | 14.5 | 29.1 | 36.3
7/8 (22) |  | 1.28 | 2.09 | 3.26 | 5.9 | 8.42 | 11.2 | 15.3 | 16.2 | 20.2 | 45 | 56.2
1 1/8 (29) |  | 2.62 | 4.26 | 6.62 | 11.9 | 17 | 22.6 | 30.8 | 27.6 | 34.4 | 82.7 | 103
1 3/8 (35) |  | 4.58 | 7.44 | 11.6 | 20.8 | 29.7 | 39.4 | 53.6 | 42 | 52.5 | 126 | 157
1 5/8 (41) |  | 7.27 | 11.8 | 18.3 | 32.9 | 46.8 | 62.1 | 84.6 | 59.4 | 74.2 | 178 | 223
2 1/8 (54) |  | 14.7 | 23.9 | 37.4 | 68.2 | 96.9 | 128 | 175 | 103 | 129 | 310 | 387
2 5/8 (67) |  | 22.7 | 36.9 | 57.6 | 106 | 153 | 227 | 308 | 159 | 199 | 478 | 598
3 1/8 (79) |  | 32.4 | 52.6 | 82.3 | 151 | 219 | 361 | 490 | 228 | 284 | 683 | 853
3 5/8 (92) |  | 43.8 | 71.2 | 111 | 204 | 296 | 535 | 727 | 308 | 385 | 924 | 1150
4 1/8 (105) |  | 56.9 | 92.6 | 145 | 266 | 385 | 754 | 1020 | 400 | 500 | 1200 | 1500
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.209 | 0.334 | 0.51 | 0.898 | 1.26 | 1.67 | 2.25 | 4.7 | 5.86 | 6.87 | 8.58
1/2 (13) | 80 | 0.414 | 0.66 | 1.01 | 1.77 | 2.49 | 3.28 | 4.43 | 7.82 | 9.77 | 13.5 | 16.9
3/4 (19) | 80 | 0.938 | 1.49 | 2.27 | 3.99 | 5.6 | 7.39 | 10 | 14.5 | 18 | 30.5 | 38.1
1 (25) | 80 | 1.84 | 2.93 | 4.45 | 7.82 | 11 | 14.5 | 19.5 | 24 | 30 | 59.8 | 74.7
1 1/4 (32) | 80 | 3.97 | 6.29 | 9.56 | 16.8 | 23.5 | 31 | 41.9 | 42.9 | 53.5 | 128 | 160
1 1/2 (38) | 80 | 6.06 | 9.6 | 14.6 | 25.6 | 35.8 | 47.2 | 63.8 | 59.1 | 73.8 | 177 | 221
2 (51) | 40 | 14.1 | 22.3 | 33.9 | 59.4 | 83.2 | 110 | 148 | 112 | 140 | 336 | 420
2 1/2 (64) | 40 | 22.5 | 35.6 | 54 | 94.6 | 133 | 175 | 236 | 160 | 200 | 480 | 599
3 (76) | 40 | 35.1 | 57.1 | 89.3 | 164 | 234 | 309 | 417 | 247 | 309 | 741 | 926
4 (102) | 40 | 60.5 | 98.4 | 154 | 282 | 409 | 628 | 848 | 425 | 531 | 1280 | 1590
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.28 | 1.19 | 1.1 | 0.9 | 0.81 | 0.72 | 0.62
| Suction Line |  | 1.2 | 1.13 | 1.07 | 0.93 | 0.86 | 0.78 | 0.71
| Discharge Line |  | 0.86 | 0.91 | 0.96 | 1.03 | 1.05 | 1.06 | 1.06
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 12
I-P
Table 12 Suction, Discharge, and Liquid Line Capacities for Refrigerant 457A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 2.78 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 3.01 psi,
Type L, |  | 0.62622 | 0.93968 | 1.3484 | 1.8641 | 2.4979 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | -40 | -20 | 0 | 20 | 40 | -40 | 40 | -40 | 40 | -40 | 40
3/8 |  | --- | --- | --- | 0.126 | 0.189 | 0.254 | 0.344 | 0.784 | 0.971 | 1.11 | 1.37
1/2 |  | --- | 0.122 | 0.199 | 0.311 | 0.467 | 0.626 | 0.845 | 1.54 | 1.91 | 2.74 | 3.39
5/8 |  | 0.128 | 0.222 | 0.362 | 0.564 | 0.845 | 1.13 | 1.53 | 2.41 | 2.98 | 4.96 | 6.15
3/4 |  | 0.22 | 0.379 | 0.618 | 0.962 | 1.44 | 1.93 | 2.6 | 3.59 | 4.45 | 8.46 | 10.5
7/8 |  | 0.341 | 0.588 | 0.958 | 1.49 | 2.22 | 2.98 | 4.01 | 4.99 | 6.18 | 13.1 | 16.2
1 1/8 |  | 0.696 | 1.2 | 1.94 | 3.02 | 4.5 | 6.02 | 8.11 | 8.51 | 10.5 | 25.5 | 31.6
1 3/8 |  | 1.22 | 2.09 | 3.4 | 5.26 | 7.84 | 10.5 | 14.1 | 13 | 16.1 | 38.9 | 48.2
1 5/8 |  | 1.93 | 3.32 | 5.38 | 8.32 | 12.4 | 16.6 | 22.3 | 18.4 | 22.7 | 55.1 | 68.2
2 1/8 |  | 3.82 | 6.56 | 10.7 | 16.8 | 25.5 | 34.2 | 46 | 31.9 | 39.5 | 95.8 | 119
2 5/8 |  | 5.89 | 10.1 | 16.5 | 26 | 39.4 | 60.4 | 81.1 | 49.2 | 61 | 148 | 183
3 1/8 |  | 8.41 | 14.4 | 23.6 | 37 | 56.2 | 96.2 | 129 | 70.3 | 87 | 211 | 261
3 5/8 |  | 11.4 | 19.5 | 31.9 | 50.1 | 76 | 143 | 192 | 95.1 | 118 | 285 | 353
4 1/8 |  | 14.8 | 25.4 | 41.5 | 65.1 | 98.8 | 193 | 270 | 124 | 153 | 371 | 459
Steel
IPS | SCH
3/8 | 80 | --- | --- | 0.15 | 0.229 | 0.336 | 0.445 | 0.595 | 1.45 | 1.8 | 2.01 | 2.49
1/2 | 80 | 0.111 | 0.186 | 0.296 | 0.451 | 0.661 | 0.877 | 1.17 | 2.42 | 2.99 | 3.97 | 4.92
3/4 | 80 | 0.251 | 0.421 | 0.668 | 1.02 | 1.49 | 1.98 | 2.64 | 4.46 | 5.53 | 8.95 | 11.1
1 | 80 | 0.494 | 0.826 | 1.31 | 1.99 | 2.92 | 3.87 | 5.16 | 7.42 | 9.19 | 17.5 | 21.7
1 1/4 | 80 | 1.06 | 1.78 | 2.81 | 4.27 | 6.25 | 8.29 | 11.1 | 13.2 | 16.4 | 37.6 | 46.6
1 1/2 | 80 | 1.62 | 2.71 | 4.29 | 6.51 | 9.53 | 12.6 | 16.8 | 18.2 | 22.6 | 54.7 | 67.7
2 | 40 | 3.78 | 6.3 | 10 | 15.1 | 22.1 | 29.3 | 39.1 | 34.6 | 42.9 | 104 | 129
2 1/2 | 40 | 5.91 | 10.1 | 15.9 | 24.1 | 35.3 | 46.7 | 62.3 | 49.4 | 61.2 | 148 | 184
3 | 40 | 9.13 | 15.7 | 25.6 | 40.2 | 61 | 82.6 | 110 | 76.3 | 94.5 | 229 | 283
4 | 40 | 15.7 | 27 | 44.1 | 69.2 | 105 | 168 | 224 | 131 | 163 | 394 | 488
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.24 | 1.15 | 1.05 | 0.95 | 0.86 | 0.76 | 0.66
| Suction Line |  | 1.17 | 1.1 | 1.04 | 0.96 | 0.89 | 0.82 | 0.74
| Discharge Line |  | 0.84 | 0.91 | 0.97 | 1.03 | 1.08 | 1.11 | 1.13
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 12 Suction, Discharge, and Liquid Line Capacities for Refrigerant 457A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 17.1 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 18.5 kPa,
Type L, |  | 3.8942 | 5.6219 | 7.8228 | 12.127 | 15.7393 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -40 | -30 | -20 | -5 | 5 | -40 | 5 | -40 | 5 | -40 | 5
3/8 (10) |  | --- | 0.157 | 0.247 | 0.453 | 0.651 | 0.848 | 1.15 | 2.74 | 3.4 | 3.72 | 4.61
1/2 (13) |  | 0.237 | 0.39 | 0.612 | 1.12 | 1.61 | 2.09 | 2.82 | 5.39 | 6.68 | 9.19 | 11.4
5/8 (16) |  | 0.433 | 0.71 | 1.11 | 2.03 | 2.91 | 3.78 | 5.1 | 8.42 | 10.4 | 16.7 | 20.7
3/4 (19) |  | 0.741 | 1.21 | 1.9 | 3.46 | 4.95 | 6.43 | 8.68 | 12.6 | 15.6 | 28.4 | 35.2
7/8 (22) |  | 1.15 | 1.88 | 2.94 | 5.35 | 7.65 | 9.93 | 13.4 | 17.5 | 21.6 | 44 | 54.5
1 1/8 (29) |  | 2.35 | 3.84 | 5.98 | 10.8 | 15.5 | 20.1 | 27.1 | 29.8 | 36.9 | 89.3 | 111
1 3/8 (35) |  | 4.12 | 6.71 | 10.5 | 18.9 | 27 | 35 | 47.1 | 45.4 | 56.2 | 136 | 169
1 5/8 (41) |  | 6.54 | 10.6 | 16.6 | 29.9 | 42.6 | 55.3 | 74.4 | 64.2 | 79.6 | 193 | 239
2 1/8 (54) |  | 13.3 | 21.7 | 34 | 62 | 88.3 | 114 | 154 | 112 | 138 | 335 | 415
2 5/8 (67) |  | 20.6 | 33.5 | 52.4 | 96.5 | 140 | 202 | 271 | 172 | 213 | 517 | 640
3 1/8 (79) |  | 29.3 | 47.8 | 74.8 | 138 | 200 | 321 | 432 | 246 | 305 | 738 | 914
3 5/8 (92) |  | 39.7 | 64.7 | 101 | 186 | 270 | 477 | 641 | 333 | 412 | 998 | 1240
4 1/8 (105) |  | 51.6 | 84.1 | 132 | 242 | 351 | 663 | 902 | 432 | 536 | 1300 | 1610
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.189 | 0.303 | 0.464 | 0.821 | 1.16 | 1.49 | 1.99 | 5.07 | 6.29 | 6.79 | 8.42
1/2 (13) | 80 | 0.375 | 0.6 | 0.917 | 1.62 | 2.28 | 2.94 | 3.92 | 8.45 | 10.5 | 13.4 | 16.6
3/4 (19) | 80 | 0.85 | 1.36 | 2.07 | 3.65 | 5.13 | 6.61 | 8.84 | 15.6 | 19.3 | 30.2 | 37.5
1 (25) | 80 | 1.67 | 2.66 | 4.06 | 7.16 | 10.1 | 13 | 17.3 | 26 | 32.2 | 59.2 | 73.4
1 1/4 (32) | 80 | 3.6 | 5.73 | 8.73 | 15.3 | 21.6 | 27.8 | 37.1 | 46.3 | 57.4 | 127 | 157
1 1/2 (38) | 80 | 5.5 | 8.74 | 13.3 | 23.4 | 32.9 | 42.3 | 56.5 | 63.8 | 79 | 191 | 237
2 (51) | 40 | 12.8 | 20.4 | 31 | 54.4 | 76.3 | 98.2 | 131 | 121 | 150 | 363 | 450
2 1/2 (64) | 40 | 20.5 | 32.5 | 49.4 | 86.7 | 122 | 157 | 209 | 173 | 214 | 518 | 642
3 (76) | 40 | 31.8 | 51.9 | 81.2 | 149 | 215 | 277 | 369 | 267 | 331 | 800 | 992
4 (102) | 40 | 54.8 | 89.4 | 140 | 257 | 373 | 563 | 751 | 459 | 569 | 1380 | 1710
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.26 | 1.17 | 1.09 | 0.91 | 0.83 | 0.74 | 0.65
| Suction Line |  | 1.18 | 1.12 | 1.06 | 0.94 | 0.87 | 0.8 | 0.73
| Discharge Line |  | 0.85 | 0.91 | 0.96 | 1.04 | 1.08 | 1.11 | 1.13
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 13
I-P
Table 13 Suction, Discharge, and Liquid Line Capacities for Refrigerant 516A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 2°F, max velocity 3000 fpm, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, psi) |  |  |  |  | (Dt = 1°F, Dp = 2.15 psi, |  | Velocity = 100 fpm |  | (Dt = 1°F, Dp = 2.15 psi,
Type L, |  | 1.0431 | 1.2343 | 1.4475 | 1.6838 | 1.9441 | max velocity 3000 fpm) |  |  |  | max velocity 300 fpm)
Copper, |  | Saturated Suction Temperature, °F
OD, in |  | 0 | 10 | 20 | 30 | 40 | 0 | 40 | 0 | 40 | 0 | 40
3/8 |  | --- | --- | --- | 0.114 | 0.14 | 0.209 | 0.241 | 0.813 | 0.917 | 0.92 | 1.04
1/2 |  | 0.143 | 0.182 | 0.227 | 0.282 | 0.346 | 0.514 | 0.594 | 1.6 | 1.8 | 2.28 | 2.57
5/8 |  | 0.261 | 0.33 | 0.413 | 0.511 | 0.627 | 0.931 | 1.08 | 2.5 | 2.81 | 4.14 | 4.67
3/4 |  | 0.445 | 0.563 | 0.704 | 0.872 | 1.07 | 1.58 | 1.83 | 3.73 | 4.2 | 7.07 | 7.97
7/8 |  | 0.69 | 0.872 | 1.09 | 1.35 | 1.65 | 2.45 | 2.83 | 5.18 | 5.84 | 10.9 | 12.3
1 1/8 |  | 1.4 | 1.77 | 2.21 | 2.73 | 3.35 | 4.95 | 5.72 | 8.83 | 10 | 22.2 | 25.1
1 3/8 |  | 2.45 | 3.09 | 3.86 | 4.77 | 5.83 | 8.62 | 9.95 | 13.5 | 15.2 | 38.8 | 43.8
1 5/8 |  | 3.88 | 4.9 | 6.11 | 7.54 | 9.22 | 13.6 | 15.7 | 19 | 21.5 | 57.1 | 64.4
2 1/8 |  | 8.07 | 10.2 | 12.7 | 15.6 | 19.1 | 28.2 | 32.5 | 33.1 | 37.3 | 99.4 | 112
2 5/8 |  | 12.9 | 16.4 | 20.6 | 25.7 | 31.7 | 49.7 | 57.3 | 51.1 | 57.6 | 153 | 173
3 1/8 |  | 18.5 | 23.4 | 29.4 | 36.6 | 45.2 | 79.1 | 91.3 | 72.9 | 82.2 | 219 | 247
3 5/8 |  | 25 | 31.7 | 39.8 | 49.5 | 61.1 | 117 | 135 | 98.6 | 111 | 296 | 334
4 1/8 |  | 32.5 | 41.2 | 51.7 | 64.4 | 79.5 | 165 | 191 | 128 | 145 | 385 | 434
Steel
IPS | SCH
3/8 | 80 | 0.109 | 0.137 | 0.169 | 0.207 | 0.251 | 0.367 | 0.423 | 1.5 | 1.7 | 1.72 | 1.93
1/2 | 80 | 0.216 | 0.27 | 0.333 | 0.408 | 0.496 | 0.722 | 0.832 | 2.51 | 2.83 | 3.39 | 3.82
3/4 | 80 | 0.487 | 0.609 | 0.752 | 0.921 | 1.12 | 1.63 | 1.87 | 4.63 | 5.22 | 7.64 | 8.62
1 | 80 | 0.956 | 1.19 | 1.47 | 1.8 | 2.19 | 3.19 | 3.67 | 7.7 | 8.68 | 15 | 16.9
1 1/4 | 80 | 2.05 | 2.56 | 3.16 | 3.87 | 4.69 | 6.83 | 7.86 | 13.7 | 15.5 | 32.2 | 36.3
1 1/2 | 80 | 3.13 | 3.91 | 4.83 | 5.9 | 7.15 | 10.4 | 12 | 18.9 | 21.3 | 49.1 | 55.3
2 | 40 | 7.28 | 9.08 | 11.2 | 13.7 | 16.6 | 24.2 | 27.8 | 35.9 | 40.5 | 108 | 121
2 1/2 | 40 | 11.6 | 14.5 | 17.9 | 21.9 | 26.5 | 38.5 | 44.3 | 51.2 | 57.8 | 154 | 173
3 | 40 | 20.1 | 25.4 | 31.6 | 38.6 | 46.8 | 68 | 78.3 | 79.1 | 89.2 | 237 | 268
4 | 40 | 34.5 | 43.8 | 55 | 68.4 | 84.5 | 138 | 159 | 136 | 154 | 409 | 461
Notes:
1. Table capacities are in tons of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F condensing temperature and 0°F subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a 20°F evaporator temperature, and are suitable in the range of 0°F to 40°F.
Condensing Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Liquid Line |  | 1.23 | 1.14 | 1.05 | 0.95 | 0.86 | 0.77 | 0.68
| Suction Line |  | 1.17 | 1.1 | 1.04 | 0.96 | 0.89 | 0.82 | 0.74
| Discharge Line |  | 0.84 | 0.91 | 0.97 | 1.03 | 1.07 | 1.11 | 1.13
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.
SI
Table 13 Suction, Discharge, and Liquid Line Capacities for Refrigerant 516A (Single- or High-Stage Applications)
|  | Suction Lines (Dt = 1 K, max velocity 15 m/s, |  |  |  |  | Discharge Linesc |  | Liquid Linesa,b,c
Line Size |  | corresponding Dp, kPa) |  |  |  |  | (Dt = 0.5 K, Dp = 13.2 kPa, |  | Velocity = 0.5 m/s |  | (Dt = 0.5 K, Dp = 13.2 kPa,
Type L, |  | 7.061 | 8.1845 | 9.4211 | 10.7751 | 12.2506 | max velocity 15 m/s) |  |  |  | max velocity 1.5 m/s)
Copper, |  | Saturated Suction Temperature, °C
OD, in (mm) |  | -15 | -10 | -5 | 0 | 5 | -15 | 5 | -15 | 5 | -15 | 5
3/8 (10) |  | 0.22 | 0.271 | 0.331 | 0.401 | 0.483 | 0.709 | 0.806 | 2.89 | 3.21 | 3.13 | 3.48
1/2 (13) |  | 0.545 | 0.671 | 0.819 | 0.992 | 1.19 | 1.75 | 1.98 | 5.68 | 6.31 | 7.77 | 8.63
5/8 (16) |  | 0.991 | 1.22 | 1.49 | 1.8 | 2.16 | 3.16 | 3.59 | 8.87 | 9.86 | 14.1 | 15.7
3/4 (19) |  | 1.69 | 2.08 | 2.54 | 3.07 | 3.68 | 5.38 | 6.11 | 13.2 | 14.7 | 24.1 | 26.8
7/8 (22) |  | 2.62 | 3.22 | 3.93 | 4.74 | 5.69 | 8.32 | 9.44 | 18.4 | 20.4 | 37.3 | 41.5
1 1/8 (29) |  | 5.33 | 6.55 | 7.97 | 9.62 | 11.5 | 16.8 | 19.1 | 31.4 | 34.9 | 75.9 | 84.3
1 3/8 (35) |  | 9.32 | 11.4 | 13.9 | 16.8 | 20.1 | 29.3 | 33.3 | 47.8 | 53.1 | 133 | 147
1 5/8 (41) |  | 14.8 | 18.1 | 22 | 26.5 | 31.8 | 46.3 | 52.5 | 67.6 | 75.2 | 203 | 225
2 1/8 (54) |  | 30.7 | 37.6 | 45.6 | 55 | 65.8 | 95.8 | 109 | 118 | 131 | 353 | 392
2 5/8 (67) |  | 50.9 | 62.8 | 76.8 | 93.3 | 113 | 169 | 192 | 181 | 202 | 544 | 605
3 1/8 (79) |  | 72.7 | 89.6 | 110 | 133 | 161 | 269 | 305 | 259 | 288 | 777 | 863
3 5/8 (92) |  | 98.3 | 121 | 148 | 180 | 217 | 400 | 453 | 350 | 389 | 1050 | 1170
4 1/8 (105) |  | 128 | 158 | 193 | 234 | 283 | 563 | 638 | 455 | 506 | 1370 | 1520
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.414 | 0.504 | 0.609 | 0.729 | 0.867 | 1.25 | 1.42 | 5.34 | 5.94 | 5.87 | 6.53
1/2 (13) | 80 | 0.817 | 0.995 | 1.2 | 1.44 | 1.71 | 2.46 | 2.79 | 8.9 | 9.89 | 11.6 | 12.9
3/4 (19) | 80 | 1.85 | 2.25 | 2.71 | 3.24 | 3.85 | 5.55 | 6.28 | 16.4 | 18.3 | 26.2 | 29.1
1 (25) | 80 | 3.62 | 4.41 | 5.31 | 6.36 | 7.55 | 10.9 | 12.3 | 27.3 | 30.4 | 51.4 | 57.1
1 1/4 (32) | 80 | 7.78 | 9.46 | 11.4 | 13.6 | 16.2 | 23.3 | 26.4 | 48.8 | 54.2 | 110 | 123
1 1/2 (38) | 80 | 11.9 | 14.4 | 17.4 | 20.8 | 24.7 | 35.5 | 40.2 | 67.2 | 74.7 | 168 | 187
2 (51) | 40 | 27.6 | 33.5 | 40.4 | 48.3 | 57.3 | 82.4 | 93.3 | 128 | 142 | 383 | 425
2 1/2 (64) | 40 | 44 | 53.4 | 64.4 | 77 | 91.4 | 131 | 149 | 182 | 202 | 546 | 607
3 (76) | 40 | 77.8 | 94.5 | 114 | 136 | 161 | 232 | 263 | 281 | 312 | 843 | 937
4 (102) | 40 | 136 | 167 | 205 | 249 | 300 | 472 | 534 | 484 | 538 | 1450 | 1610
Notes:
1. Table capacities are in kilowatts of refrigeration. Discharge refrigerant state is determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor. Liquid and suction refrigerant states are at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C condensing temperature and 0 K subcooling. Multiply capacities by the following correction factors for other condensing temperatures. Correction factors based on a -5°C evaporator temperature, and are suitable in the range of -15°C to 5°C.
Condensing Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Liquid Line |  | 1.24 | 1.16 | 1.08 | 0.92 | 0.84 | 0.76 | 0.68
| Suction Line |  | 1.18 | 1.12 | 1.06 | 0.94 | 0.87 | 0.81 | 0.74
| Discharge Line |  | 0.82 | 0.88 | 0.94 | 1.05 | 1.09 | 1.13 | 1.15
aSizing shown is recommended where any gas generated in receiver must return up condensate line to condenser without restricting condensate flow. Water-cooled condensers, where receiver ambient temperature may be higher than refrigerant condensing temperature, fall into this category.
bLine pressure drop Dp is conservative; if subcooling is substantial or line is short, a smaller size line may be used. Applications with very little subcooling or very long lines may require a larger line.
cSystem working pressures may exceed calculated allowable pressure in some listed type L annealed copper tubes at certain saturated condensing temperatures. Review working pressure allowances for the pipe material used before selecting pipe sizes to ensure the pipe is properly rated for system working and design pressures.

## Table 14
I-P
Table 14 Suction Line Capacities in Tons for Refrigerant 454B (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.58 psi | Dp = 0.29 psi | Dp = 0.84 psi | Dp = 0.42 psi | Dp = 1.17 psi | Dp = 0.59 psi | Dp = 1.58 psi | Dp = 0.79 psi | Dp = 2.08 psi | Dp = 1,04 psi
3/8 |  | --- | --- | --- | --- | 0.124 | --- | 0.185 | 0.126 | 0.266 | 0.181
1/2 |  | 0.121 | --- | 0.198 | 0.134 | 0.307 | 0.209 | 0.456 | 0.311 | 0.655 | 0.448
5/8 |  | 0.221 | 0.15 | 0.36 | 0.245 | 0.557 | 0.38 | 0.827 | 0.566 | 1.19 | 0.813
3/4 |  | 0.379 | 0.258 | 0.615 | 0.42 | 0.951 | 0.65 | 1.41 | 0.966 | 2.02 | 1.39
7/8 |  | 0.588 | 0.401 | 0.954 | 0.652 | 1.47 | 1.01 | 2.18 | 1.5 | 3.12 | 2.15
1 1/8 |  | 1.2 | 0.819 | 1.94 | 1.33 | 2.99 | 2.05 | 4.42 | 3.04 | 6.32 | 4.35
1 3/8 |  | 2.1 | 1.44 | 3.39 | 2.33 | 5.22 | 3.59 | 7.71 | 5.31 | 11 | 7.59
1 5/8 |  | 3.33 | 2.28 | 5.38 | 3.69 | 8.27 | 5.69 | 12.2 | 8.41 | 17.4 | 12
2 1/8 |  | 6.95 | 4.77 | 11.2 | 7.7 | 17.2 | 11.8 | 25.3 | 17.5 | 36 | 24.9
2 5/8 |  | 12.3 | 8.47 | 19.8 | 13.7 | 30.4 | 21 | 44.7 | 30.9 | 63.5 | 44
3 1/8 |  | 17.9 | 13.6 | 29.1 | 21.8 | 45.3 | 33.5 | 68.1 | 49.4 | 99.3 | 70.3
3 5/8 |  | 24.2 | 20.2 | 39.4 | 32.5 | 61.3 | 49.9 | 92.1 | 73.4 | 134 | 104
4 1/8 |  | 31.5 | 28.6 | 51.2 | 46 | 79.7 | 70.4 | 120 | 104 | 175 | 147
Steel
IPS | SCH
3/8 | 80 | --- | --- | 0.153 | 0.106 | 0.231 | 0.161 | 0.335 | 0.235 | 0.471 | 0.331
1/2 | 80 | 0.19 | 0.133 | 0.302 | 0.211 | 0.455 | 0.319 | 0.661 | 0.464 | 0.929 | 0.654
3/4 | 80 | 0.431 | 0.301 | 0.682 | 0.478 | 1.03 | 0.722 | 1.49 | 1.05 | 2.09 | 1.47
1 | 80 | 0.849 | 0.593 | 1.34 | 0.939 | 2.02 | 1.42 | 2.92 | 2.06 | 4.1 | 2.89
1 1/4 | 80 | 1.83 | 1.28 | 2.88 | 2.02 | 4.33 | 3.05 | 6.27 | 4.42 | 8.79 | 6.2
1 1/2 | 80 | 2.79 | 1.96 | 4.39 | 3.09 | 6.6 | 4.65 | 9.56 | 6.74 | 13.4 | 9.45
2 | 40 | 6.5 | 4.56 | 10.2 | 7.19 | 15.3 | 10.8 | 22.2 | 15.7 | 31.1 | 22
2 1/2 | 40 | 10.4 | 7.29 | 16.3 | 11.5 | 24.5 | 17.3 | 35.4 | 25 | 49.6 | 35
3 | 40 | 18.4 | 12.9 | 28.8 | 20.3 | 43.3 | 30.5 | 62.5 | 44.2 | 87.6 | 61.9
4 | 40 | 33.5 | 26.4 | 54.4 | 41.4 | 84.7 | 62.2 | 127 | 90 | 178 | 126
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.14 | 1.09 | 1.03 | 0.97 | 0.91 | 0.84 | 0.77
SI
Table 14 Suction Line Capacities in Tons for Refrigerant 454B (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 3.58 kPa | Dp = 1.80 kPa | Dp = 5.02 kPa | Dp = 2.52 kPa | Dp = 6.82 kPa | Dp = 3.42 kPa | Dp = 10.3 kPa | Dp = 5.14 kPa | Dp = 13.1 kPa | Dp = 6.56 kPa
3/8 (10) |  | 0.164 | 0.11 | 0.255 | 0.173 | 0.383 | 0.26 | 0.658 | 0.448 | 0.91 | 0.621
1/2 (13) |  | 0.408 | 0.276 | 0.635 | 0.431 | 0.949 | 0.646 | 1.62 | 1.11 | 2.24 | 1.54
5/8 (16) |  | 0.744 | 0.505 | 1.16 | 0.787 | 1.72 | 1.18 | 2.95 | 2.02 | 4.06 | 2.79
3/4 (19) |  | 1.28 | 0.867 | 1.98 | 1.35 | 2.95 | 2.01 | 5.02 | 3.44 | 6.92 | 4.75
7/8 (22) |  | 1.98 | 1.35 | 3.07 | 2.1 | 4.57 | 3.12 | 7.77 | 5.33 | 10.7 | 7.36
1 1/8 (29) |  | 4.04 | 2.76 | 6.25 | 4.28 | 9.28 | 6.36 | 15.8 | 10.8 | 21.7 | 14.9
1 3/8 (35) |  | 7.08 | 4.84 | 10.9 | 7.49 | 16.2 | 11.1 | 27.5 | 18.9 | 37.7 | 26
1 5/8 (41) |  | 11.2 | 7.69 | 17.3 | 11.9 | 25.7 | 17.6 | 43.5 | 30 | 59.7 | 41.2
2 1/8 (54) |  | 23.4 | 16.1 | 36.1 | 24.8 | 53.3 | 36.7 | 90.1 | 62.2 | 124 | 85.4
2 5/8 (67) |  | 41.6 | 28.5 | 63.9 | 44 | 94.4 | 65.1 | 159 | 110 | 218 | 151
3 1/8 (79) |  | 62.4 | 45.7 | 96.8 | 70.4 | 145 | 104 | 251 | 176 | 347 | 241
3 5/8 (92) |  | 84.4 | 68.2 | 131 | 105 | 196 | 155 | 340 | 261 | 476 | 358
4 1/8 (105) |  | 110 | 96.4 | 170 | 148 | 255 | 219 | 442 | 369 | 619 | 505
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.325 | 0.225 | 0.493 | 0.344 | 0.72 | 0.503 | 1.2 | 0.838 | 1.62 | 1.14
1/2 (13) | 80 | 0.643 | 0.447 | 0.975 | 0.681 | 1.42 | 1 | 2.36 | 1.65 | 3.19 | 2.24
3/4 (19) | 80 | 1.46 | 1.02 | 2.21 | 1.54 | 3.21 | 2.25 | 5.31 | 3.74 | 7.19 | 5.06
1 (25) | 80 | 2.87 | 2 | 4.34 | 3.04 | 6.3 | 4.43 | 10.4 | 7.33 | 14.1 | 9.93
1 1/4 (32) | 80 | 6.17 | 4.32 | 9.32 | 6.54 | 13.5 | 9.52 | 22.3 | 15.7 | 30.2 | 21.3
1 1/2 (38) | 80 | 9.43 | 6.61 | 14.2 | 10 | 20.6 | 14.5 | 34.1 | 24 | 46 | 32.5
2 (51) | 40 | 22 | 15.4 | 33.1 | 23.3 | 48 | 33.8 | 79.1 | 55.8 | 107 | 75.5
2 1/2 (64) | 40 | 35.1 | 24.7 | 52.8 | 37.2 | 76.6 | 54 | 126 | 89 | 170 | 120
3 (76) | 40 | 62.1 | 43.7 | 93.4 | 65.8 | 135 | 95.5 | 223 | 157 | 301 | 213
4 (102) | 40 | 117 | 89.2 | 181 | 134 | 271 | 195 | 454 | 321 | 613 | 433
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.15 | 1.1 | 1.05 | 0.95 | 0.89 | 0.83 | 0.77

## Table 15
I-P
Table 15 Suction Line Capacities in Tons for Refrigerants 448A/449A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.39 psi | Dp = 0.20 psi | Dp = 0.59 psi | Dp = 0.30 psi | Dp = 0.85 psi | Dp = 0.43 psi | Dp = 1.17 psi | Dp = 0.59 psi | Dp = 1.56 psi | Dp = 0.78 psi
3/8 |  | --- | --- | --- | --- | --- | --- | 0.108 | --- | 0.161 | 0.11
1/2 |  | --- | --- | 0.105 | --- | 0.171 | 0.117 | 0.267 | 0.182 | 0.398 | 0.272
5/8 |  | 0.111 | --- | 0.191 | 0.13 | 0.312 | 0.212 | 0.484 | 0.331 | 0.722 | 0.494
3/4 |  | 0.19 | 0.129 | 0.327 | 0.223 | 0.532 | 0.364 | 0.826 | 0.565 | 1.23 | 0.844
7/8 |  | 0.295 | 0.201 | 0.508 | 0.346 | 0.825 | 0.564 | 1.28 | 0.876 | 1.9 | 1.31
1 1/8 |  | 0.603 | 0.411 | 1.03 | 0.707 | 1.68 | 1.15 | 2.59 | 1.78 | 3.85 | 2.65
1 3/8 |  | 1.06 | 0.722 | 1.81 | 1.24 | 2.93 | 2.01 | 4.53 | 3.11 | 6.72 | 4.63
1 5/8 |  | 1.68 | 1.15 | 2.87 | 1.97 | 4.65 | 3.19 | 7.16 | 4.93 | 10.6 | 7.33
2 1/8 |  | 3.5 | 2.4 | 5.98 | 4.11 | 9.65 | 6.65 | 14.9 | 10.3 | 22 | 15.2
2 5/8 |  | 6.22 | 4.27 | 10.6 | 7.3 | 17.1 | 11.8 | 26.3 | 18.2 | 38.9 | 26.9
3 1/8 |  | 10 | 6.84 | 17 | 11.7 | 27.3 | 18.8 | 41.9 | 29 | 61.9 | 42.9
3 5/8 |  | 14.1 | 10.2 | 24.2 | 17.4 | 39.5 | 28 | 61.8 | 43.1 | 92 | 63.8
4 1/8 |  | 18.4 | 14.4 | 31.5 | 24.6 | 51.3 | 39.6 | 80.4 | 60.9 | 122 | 90
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.131 | --- | 0.199 | 0.139 | 0.29 | 0.204
1/2 | 80 | --- | --- | 0.163 | 0.114 | 0.258 | 0.181 | 0.392 | 0.275 | 0.572 | 0.402
3/4 | 80 | 0.22 | 0.153 | 0.369 | 0.258 | 0.584 | 0.409 | 0.884 | 0.621 | 1.29 | 0.907
1 | 80 | 0.434 | 0.303 | 0.725 | 0.507 | 1.15 | 0.805 | 1.73 | 1.22 | 2.53 | 1.78
1 1/4 | 80 | 0.935 | 0.654 | 1.56 | 1.09 | 2.46 | 1.73 | 3.72 | 2.62 | 5.41 | 3.82
1 1/2 | 80 | 1.43 | 1 | 2.38 | 1.67 | 3.76 | 2.64 | 5.67 | 4 | 8.25 | 5.82
2 | 40 | 3.33 | 2.34 | 5.54 | 3.9 | 8.73 | 6.15 | 13.2 | 9.29 | 19.2 | 13.5
2 1/2 | 40 | 5.32 | 3.74 | 8.84 | 6.22 | 13.9 | 9.82 | 21 | 14.8 | 30.6 | 21.6
3 | 40 | 9.42 | 6.62 | 15.6 | 11 | 24.6 | 17.4 | 37.1 | 26.2 | 54 | 38.1
4 | 40 | 19.2 | 13.5 | 31.9 | 22.5 | 50.2 | 35.4 | 75.6 | 53.4 | 110 | 77.7
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.17 | 1.11 | 1.04 | 0.96 | 0.89 | 0.81 | 0.73
SI
Table 15 Suction Line Capacities in Tons for Refrigerants 448A/449A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 2.45 kPa | Dp = 1.23 kPa | Dp = 3.53 kPa | Dp = 1.77 kPa | Dp = 4.91 kPa | Dp = 2.46 kPa | Dp = 7.59 kPa | Dp = 3.81 kPa | Dp = 9.83 kPa | Dp = 4.93 kPa
3/8 (10) |  | --- | --- | 0.135 | --- | 0.212 | 0.143 | 0.387 | 0.263 | 0.554 | 0.378
1/2 (13) |  | 0.204 | 0.138 | 0.336 | 0.228 | 0.526 | 0.357 | 0.957 | 0.652 | 1.37 | 0.935
5/8 (16) |  | 0.373 | 0.253 | 0.612 | 0.416 | 0.957 | 0.652 | 1.74 | 1.19 | 2.48 | 1.7
3/4 (19) |  | 0.64 | 0.435 | 1.05 | 0.713 | 1.64 | 1.12 | 2.96 | 2.03 | 4.23 | 2.9
7/8 (22) |  | 1 | 0.677 | 1.63 | 1.11 | 2.54 | 1.73 | 4.59 | 3.14 | 6.54 | 4.49
1 1/8 (29) |  | 2.03 | 1.39 | 3.32 | 2.27 | 5.16 | 3.53 | 9.31 | 6.39 | 13.3 | 9.12
1 3/8 (35) |  | 3.57 | 2.44 | 5.81 | 3.97 | 9.02 | 6.19 | 16.2 | 11.2 | 23.1 | 15.9
1 5/8 (41) |  | 5.67 | 3.88 | 9.22 | 6.31 | 14.3 | 9.82 | 25.7 | 17.7 | 36.5 | 25.2
2 1/8 (54) |  | 11.8 | 8.11 | 19.2 | 13.2 | 29.7 | 20.5 | 53.4 | 36.8 | 75.7 | 52.3
2 5/8 (67) |  | 21 | 14.4 | 34.1 | 23.4 | 52.7 | 36.3 | 94.3 | 65.1 | 134 | 92.5
3 1/8 (79) |  | 33.7 | 23.1 | 54.5 | 37.5 | 84.2 | 58 | 151 | 104 | 213 | 148
3 5/8 (92) |  | 49.3 | 34.5 | 80.2 | 55.9 | 125 | 86.4 | 224 | 155 | 317 | 219
4 1/8 (105) |  | 64.1 | 48.8 | 104 | 79 | 163 | 122 | 299 | 218 | 432 | 310
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.165 | 0.114 | 0.265 | 0.184 | 0.405 | 0.282 | 0.713 | 0.499 | 1 | 0.701
1/2 (13) | 80 | 0.328 | 0.228 | 0.525 | 0.365 | 0.8 | 0.559 | 1.41 | 0.986 | 1.97 | 1.38
3/4 (19) | 80 | 0.746 | 0.519 | 1.19 | 0.83 | 1.81 | 1.27 | 3.17 | 2.23 | 4.44 | 3.12
1 (25) | 80 | 1.47 | 1.02 | 2.34 | 1.63 | 3.55 | 2.49 | 6.22 | 4.38 | 8.7 | 6.13
1 1/4 (32) | 80 | 3.17 | 2.21 | 5.03 | 3.52 | 7.64 | 5.36 | 13.3 | 9.4 | 18.7 | 13.2
1 1/2 (38) | 80 | 4.84 | 3.38 | 7.68 | 5.39 | 11.7 | 8.19 | 20.4 | 14.3 | 28.4 | 20.1
2 (51) | 40 | 11.3 | 7.91 | 17.9 | 12.6 | 27.1 | 19.1 | 47.3 | 33.3 | 66.1 | 46.6
2 1/2 (64) | 40 | 18 | 12.6 | 28.5 | 20.1 | 43.2 | 30.5 | 75.4 | 53.2 | 105 | 74.3
3 (76) | 40 | 31.9 | 22.4 | 50.5 | 35.5 | 76.5 | 53.9 | 133 | 94.1 | 186 | 131
4 (102) | 40 | 65.2 | 45.8 | 103 | 72.5 | 156 | 110 | 217 | 192 | 379 | 268
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.19 | 1.13 | 1.06 | 0.93 | 0.87 | 0.8 | 0.72

## Table 16
I-P
Table 16 Suction Line Capacities in Tons for Refrigerant 32 (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -20 |  | -10 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.93 psi | Dp = 0.47 psi | Dp = 1.11 psi | Dp = 0.56 psi | Dp = 1.31 psi | Dp = 0.66 psi | Dp = 1.76 psi | Dp = 0.89 psi | Dp = 2.32 psi | Dp = 1.16 psi
3/8 |  | 0.105 | --- | 0.131 | --- | 0.161 | 0.11 | 0.238 | 0.162 | 0.34 | 0.232
1/2 |  | 0.26 | 0.177 | 0.324 | 0.221 | 0.4 | 0.272 | 0.589 | 0.402 | 0.838 | 0.573
5/8 |  | 0.473 | 0.322 | 0.59 | 0.402 | 0.726 | 0.496 | 1.07 | 0.731 | 1.52 | 1.04
3/4 |  | 0.81 | 0.552 | 1.01 | 0.688 | 1.24 | 0.848 | 1.82 | 1.25 | 2.58 | 1.77
7/8 |  | 1.26 | 0.858 | 1.56 | 1.07 | 1.92 | 1.31 | 2.82 | 1.93 | 3.99 | 2.74
1 1/8 |  | 2.55 | 1.75 | 3.17 | 2.18 | 3.9 | 2.68 | 5.71 | 3.93 | 8.08 | 5.57
1 3/8 |  | 4.47 | 3.06 | 5.55 | 3.81 | 6.81 | 4.68 | 10 | 6.86 | 14.1 | 9.71
1 5/8 |  | 7.08 | 4.86 | 8.78 | 6.04 | 10.8 | 7.42 | 15.8 | 10.9 | 22.2 | 15.4
2 1/8 |  | 14.7 | 10.1 | 18.3 | 12.6 | 22.4 | 15.4 | 32.6 | 22.6 | 46 | 31.9
2 5/8 |  | 24.5 | 18 | 30.5 | 22.3 | 37.7 | 27.3 | 56.2 | 39.9 | 81.2 | 56.3
3 1/8 |  | 34.9 | 28.7 | 43.6 | 35.6 | 53.9 | 43.7 | 80.2 | 63.7 | 116 | 89.8
3 5/8 |  | 47.3 | 42.8 | 59 | 53 | 72.9 | 65 | 108 | 94.7 | 157 | 133
4 1/8 |  | 61.4 | 60.5 | 76.6 | 74.9 | 94.7 | 91.7 | 141 | 134 | 204 | 188
Steel
IPS | SCH
3/8 | 80 | 0.201 | 0.14 | 0.247 | 0.173 | 0.3 | 0.21 | 0.432 | 0.303 | 0.602 | 0.423
1/2 | 80 | 0.397 | 0.277 | 0.487 | 0.341 | 0.593 | 0.416 | 0.853 | 0.599 | 1.19 | 0.835
3/4 | 80 | 0.897 | 0.628 | 1.1 | 0.773 | 1.34 | 0.94 | 1.92 | 1.35 | 2.67 | 1.88
1 | 80 | 1.76 | 1.24 | 2.16 | 1.52 | 2.63 | 1.85 | 3.77 | 2.65 | 5.24 | 3.69
1 1/4 | 80 | 3.78 | 2.66 | 4.64 | 3.26 | 5.64 | 3.97 | 8.08 | 5.7 | 11.2 | 7.92
1 1/2 | 80 | 5.77 | 4.06 | 7.08 | 4.98 | 8.6 | 6.05 | 12.3 | 8.69 | 17.1 | 12.1
2 | 40 | 13.4 | 9.46 | 16.5 | 11.6 | 20 | 14.1 | 28.6 | 20.2 | 39.7 | 28
2 1/2 | 40 | 21.4 | 15.1 | 26.3 | 18.5 | 31.9 | 22.5 | 45.6 | 32.2 | 63.3 | 44.7
3 | 40 | 37.9 | 26.7 | 46.4 | 32.7 | 56.3 | 39.7 | 80.6 | 56.9 | 112 | 79
4 | 40 | 65.3 | 54.5 | 81.5 | 66.8 | 101 | 81 | 150 | 116 | 217 | 161
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 10°F evaporator temperature, and are suitable in the range of -20°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.12 | 1.07 | 1.02 | 0.97 | 0.92 | 0.87 | 0.81
SI
Table 16 Suction Line Capacities in Tons for Refrigerant 32 (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -30 |  | -20 |  | -10 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 5.60 kPa | Dp = 2.81 kPa | Dp = 7.60 kPa | Dp = 3.81 kPa | Dp = 10.0 kPa | Dp = 5.04 kPa | Dp = 11.4 kPa | Dp = 5.73 kPa | Dp = 14.6 kPa | Dp = 7.31 kPa
3/8 (10) |  | 0.336 | 0.228 | 0.5 | 0.339 | 0.716 | 0.487 | 0.848 | 0.577 | 1.16 | 0.793
1/2 (13) |  | 0.836 | 0.568 | 1.24 | 0.843 | 1.77 | 1.21 | 2.09 | 1.43 | 2.87 | 1.96
5/8 (16) |  | 1.52 | 1.04 | 2.25 | 1.54 | 3.21 | 2.2 | 3.8 | 2.6 | 5.19 | 3.56
3/4 (19) |  | 2.6 | 1.78 | 3.85 | 2.63 | 5.48 | 3.75 | 6.47 | 4.44 | 8.84 | 6.07
7/8 (22) |  | 4.04 | 2.76 | 5.96 | 4.08 | 8.49 | 5.82 | 10 | 6.87 | 13.7 | 9.4
1 1/8 (29) |  | 8.22 | 5.63 | 12.1 | 8.3 | 17.2 | 11.8 | 20.3 | 14 | 27.7 | 19.1
1 3/8 (35) |  | 14.4 | 9.86 | 21.2 | 14.5 | 30.1 | 20.7 | 35.4 | 24.4 | 48.2 | 33.3
1 5/8 (41) |  | 22.8 | 15.6 | 33.5 | 23 | 47.5 | 32.7 | 56 | 38.6 | 76.2 | 52.6
2 1/8 (54) |  | 47.5 | 32.6 | 69.6 | 47.9 | 98.6 | 68.1 | 116 | 80.2 | 158 | 109
2 5/8 (67) |  | 81.4 | 57.9 | 121 | 84.9 | 174 | 120 | 205 | 142 | 278 | 193
3 1/8 (79) |  | 116 | 92.6 | 172 | 136 | 248 | 192 | 295 | 226 | 410 | 308
3 5/8 (92) |  | 157 | 138 | 233 | 202 | 336 | 286 | 399 | 337 | 555 | 457
4 1/8 (105) |  | 204 | 195 | 303 | 285 | 437 | 404 | 519 | 475 | 722 | 645
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.649 | 0.452 | 0.939 | 0.656 | 1.31 | 0.921 | 1.54 | 1.08 | 2.07 | 1.45
1/2 (13) | 80 | 1.28 | 0.896 | 1.85 | 1.3 | 2.59 | 1.82 | 3.03 | 2.13 | 4.07 | 2.86
3/4 (19) | 80 | 2.9 | 2.03 | 4.19 | 2.94 | 5.85 | 4.11 | 6.84 | 4.81 | 9.17 | 6.46
1 (25) | 80 | 5.7 | 4 | 8.22 | 5.77 | 11.5 | 8.07 | 13.4 | 9.43 | 18 | 12.7
1 1/4 (32) | 80 | 12.3 | 8.6 | 17.6 | 12.4 | 24.6 | 17.3 | 28.7 | 20.3 | 38.5 | 27.2
1 1/2 (38) | 80 | 18.7 | 13.1 | 26.9 | 18.9 | 37.5 | 26.4 | 43.8 | 30.9 | 58.7 | 41.4
2 (51) | 40 | 43.5 | 30.6 | 62.6 | 44.1 | 87.1 | 61.5 | 102 | 71.8 | 136 | 96.3
2 1/2 (64) | 40 | 69.4 | 48.9 | 100 | 70.3 | 139 | 98 | 162 | 115 | 217 | 153
3 (76) | 40 | 123 | 86.5 | 176 | 124 | 246 | 173 | 287 | 202 | 384 | 271
4 (102) | 40 | 217 | 176 | 322 | 254 | 454 | 353 | 552 | 412 | 767 | 552
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -12°C evaporator temperature, and are suitable in the range of -30°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.13 | 1.09 | 1.04 | 0.95 | 0.91 | 0.86 | 0.8

## Table 17
I-P
Table 17 Suction Line Capacities in Tons for Refrigerant 454A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.42 psi | Dp = 0.21 psi | Dp = 0.63 psi | Dp = 0.32 psi | Dp = 0.89 psi | Dp = 0.45 psi | Dp = 1.22 psi | Dp = 0.61 psi | Dp = 1.62 psi | Dp = 0.81 psi
3/8 |  | --- | --- | --- | --- | --- | --- | 0.115 | --- | 0.171 | 0.117
1/2 |  | --- | --- | 0.115 | --- | 0.186 | 0.126 | 0.285 | 0.195 | 0.422 | 0.289
5/8 |  | 0.124 | --- | 0.21 | 0.143 | 0.337 | 0.23 | 0.518 | 0.354 | 0.765 | 0.524
3/4 |  | 0.212 | 0.144 | 0.359 | 0.245 | 0.576 | 0.394 | 0.883 | 0.605 | 1.3 | 0.894
7/8 |  | 0.33 | 0.225 | 0.558 | 0.381 | 0.893 | 0.611 | 1.37 | 0.937 | 2.02 | 1.38
1 1/8 |  | 0.674 | 0.46 | 1.14 | 0.777 | 1.82 | 1.24 | 2.77 | 1.91 | 4.08 | 2.81
1 3/8 |  | 1.18 | 0.807 | 1.99 | 1.36 | 3.17 | 2.18 | 4.84 | 3.33 | 7.12 | 4.91
1 5/8 |  | 1.87 | 1.28 | 3.15 | 2.16 | 5.02 | 3.45 | 7.66 | 5.28 | 11.2 | 7.76
2 1/8 |  | 3.91 | 2.68 | 6.56 | 4.51 | 10.4 | 7.19 | 15.9 | 11 | 23.3 | 16.1
2 5/8 |  | 6.94 | 4.77 | 11.6 | 8 | 18.5 | 12.7 | 28.1 | 19.4 | 41.2 | 28.5
3 1/8 |  | 11.1 | 7.64 | 18.6 | 12.8 | 29.5 | 20.4 | 44.8 | 31 | 65.6 | 45.5
3 5/8 |  | 15.3 | 11.4 | 25.8 | 19.1 | 41.5 | 30.3 | 64.3 | 46.1 | 96.4 | 67.6
4 1/8 |  | 19.9 | 16.1 | 33.5 | 27 | 54 | 42.8 | 83.6 | 65.1 | 125 | 95.3
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.141 | --- | 0.212 | 0.149 | 0.307 | 0.216
1/2 | 80 | 0.108 | --- | 0.178 | 0.124 | 0.279 | 0.195 | 0.418 | 0.293 | 0.605 | 0.425
3/4 | 80 | 0.245 | 0.171 | 0.403 | 0.282 | 0.63 | 0.442 | 0.943 | 0.663 | 1.36 | 0.96
1 | 80 | 0.482 | 0.336 | 0.792 | 0.555 | 1.24 | 0.868 | 1.85 | 1.3 | 2.67 | 1.88
1 1/4 | 80 | 1.04 | 0.726 | 1.7 | 1.19 | 2.65 | 1.87 | 3.97 | 2.79 | 5.73 | 4.04
1 1/2 | 80 | 1.59 | 1.11 | 2.6 | 1.83 | 4.05 | 2.85 | 6.05 | 4.26 | 8.73 | 6.16
2 | 40 | 3.7 | 2.59 | 6.05 | 4.26 | 9.42 | 6.63 | 14.1 | 9.92 | 20.3 | 14.3
2 1/2 | 40 | 5.9 | 4.15 | 9.65 | 6.8 | 15 | 10.6 | 22.4 | 15.8 | 32.3 | 22.8
3 | 40 | 10.5 | 7.35 | 17.1 | 12 | 26.5 | 18.7 | 39.6 | 28 | 57.1 | 40.3
4 | 40 | 21.1 | 15 | 34.8 | 24.5 | 54.1 | 38.2 | 80.7 | 57 | 116 | 82.2
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.17 | 1.11 | 1.04 | 0.96 | 0.89 | 0.81 | 0.73
SI
Table 17 Suction Line Capacities in Tons for Refrigerant 454A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 2.64 kPa | Dp = 1.32 kPa | Dp = 3.76 kPa | Dp = 1.89 kPa | Dp = 5.17 kPa | Dp = 2.60 kPa | Dp = 7.91 kPa | Dp = 3.97 kPa | Dp = 10.2 kPa | Dp = 5.11 kPa
3/8 (10) |  | --- | --- | 0.148 | 0.1 | 0.23 | 0.156 | 0.413 | 0.281 | 0.588 | 0.4
1/2 (13) |  | 0.229 | 0.155 | 0.37 | 0.251 | 0.571 | 0.388 | 1.02 | 0.697 | 1.45 | 0.991
5/8 (16) |  | 0.418 | 0.283 | 0.674 | 0.458 | 1.04 | 0.708 | 1.86 | 1.27 | 2.63 | 1.8
3/4 (19) |  | 0.716 | 0.487 | 1.15 | 0.785 | 1.78 | 1.21 | 3.17 | 2.17 | 4.48 | 3.07
7/8 (22) |  | 1.11 | 0.758 | 1.79 | 1.22 | 2.75 | 1.88 | 4.9 | 3.36 | 6.93 | 4.76
1 1/8 (29) |  | 2.27 | 1.55 | 3.65 | 2.49 | 5.6 | 3.83 | 9.94 | 6.83 | 14 | 9.66
1 3/8 (35) |  | 3.99 | 2.72 | 6.39 | 4.37 | 9.79 | 6.71 | 17.4 | 11.9 | 24.5 | 16.9
1 5/8 (41) |  | 6.33 | 4.33 | 10.1 | 6.94 | 15.5 | 10.7 | 27.5 | 18.9 | 38.7 | 26.7
2 1/8 (54) |  | 13.2 | 9.05 | 21.1 | 14.5 | 32.3 | 22.2 | 57 | 39.3 | 80.1 | 55.4
2 5/8 (67) |  | 23.4 | 16.1 | 37.4 | 25.7 | 57.1 | 39.3 | 101 | 69.6 | 142 | 97.9
3 1/8 (79) |  | 37.5 | 25.8 | 59.8 | 41.2 | 91.2 | 62.9 | 161 | 111 | 226 | 156
3 5/8 (92) |  | 53.3 | 38.5 | 85.5 | 61.4 | 132 | 93.7 | 239 | 165 | 335 | 232
4 1/8 (105) |  | 69.3 | 54.4 | 111 | 86.7 | 172 | 132 | 310 | 233 | 445 | 328
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.184 | 0.127 | 0.29 | 0.202 | 0.438 | 0.306 | 0.76 | 0.532 | 1.06 | 0.742
1/2 (13) | 80 | 0.365 | 0.253 | 0.575 | 0.401 | 0.866 | 0.605 | 1.5 | 1.05 | 2.08 | 1.46
3/4 (19) | 80 | 0.829 | 0.577 | 1.3 | 0.909 | 1.96 | 1.37 | 3.38 | 2.38 | 4.7 | 3.3
1 (25) | 80 | 1.63 | 1.14 | 2.56 | 1.79 | 3.84 | 2.7 | 6.63 | 4.66 | 9.2 | 6.48
1 1/4 (32) | 80 | 3.51 | 2.46 | 5.5 | 3.86 | 8.25 | 5.8 | 14.2 | 10 | 19.7 | 13.9
1 1/2 (38) | 80 | 5.37 | 3.76 | 8.4 | 5.89 | 12.6 | 8.86 | 21.7 | 15.3 | 30.1 | 21.2
2 (51) | 40 | 12.5 | 8.78 | 19.6 | 13.7 | 29.3 | 20.6 | 50.4 | 35.5 | 69.9 | 49.3
2 1/2 (64) | 40 | 20 | 14 | 31.2 | 22 | 46.7 | 32.9 | 80.3 | 56.7 | 111 | 78.6
3 (76) | 40 | 35.4 | 24.9 | 55.2 | 38.9 | 82.6 | 58.2 | 142 | 100 | 197 | 139
4 (102) | 40 | 72.3 | 50.8 | 113 | 79.3 | 168 | 119 | 289 | 204 | 401 | 283
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.19 | 1.13 | 1.06 | 0.93 | 0.87 | 0.8 | 0.72

## Table 18
I-P
Table 18 Suction Line Capacities in Tons for Refrigerant 454C (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.35 psi | Dp = 0.18 psi | Dp = 0.52 psi | Dp = 0.26 psi | Dp = 0.74 psi | Dp = 0.37 psi | Dp = 1.02 psi | Dp = 0.51 psi | Dp = 1.37 psi | Dp = 0.69 psi
3/8 |  | --- | --- | --- | --- | --- | --- | --- | --- | 0.134 | ---
1/2 |  | --- | --- | --- | --- | 0.14 | --- | 0.22 | 0.15 | 0.33 | 0.225
5/8 |  | --- | --- | 0.156 | 0.106 | 0.255 | 0.174 | 0.399 | 0.272 | 0.598 | 0.41
3/4 |  | 0.155 | 0.105 | 0.267 | 0.182 | 0.437 | 0.298 | 0.681 | 0.466 | 1.02 | 0.699
7/8 |  | 0.241 | 0.164 | 0.415 | 0.283 | 0.677 | 0.463 | 1.05 | 0.722 | 1.58 | 1.08
1 1/8 |  | 0.491 | 0.335 | 0.846 | 0.578 | 1.38 | 0.943 | 2.14 | 1.47 | 3.2 | 2.2
1 3/8 |  | 0.862 | 0.589 | 1.48 | 1.01 | 2.41 | 1.65 | 3.74 | 2.57 | 5.58 | 3.84
1 5/8 |  | 1.37 | 0.936 | 2.35 | 1.61 | 3.81 | 2.62 | 5.91 | 4.07 | 8.82 | 6.08
2 1/8 |  | 2.86 | 1.96 | 4.89 | 3.36 | 7.93 | 5.46 | 12.3 | 8.46 | 18.3 | 12.6
2 5/8 |  | 5.07 | 3.48 | 8.67 | 5.97 | 14 | 9.68 | 21.7 | 15 | 32.3 | 22.3
3 1/8 |  | 8.13 | 5.58 | 13.9 | 9.55 | 22.4 | 15.5 | 34.7 | 24 | 51.5 | 35.7
3 5/8 |  | 11.9 | 8.33 | 20.4 | 14.2 | 33.4 | 23 | 51.5 | 35.6 | 76.5 | 53
4 1/8 |  | 15.4 | 11.8 | 26.5 | 20.1 | 43.4 | 32.5 | 68.1 | 50.3 | 104 | 74.8
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.108 | --- | 0.164 | 0.115 | 0.242 | 0.17
1/2 | 80 | --- | --- | 0.133 | --- | 0.213 | 0.149 | 0.325 | 0.228 | 0.477 | 0.335
3/4 | 80 | 0.18 | 0.125 | 0.302 | 0.211 | 0.481 | 0.337 | 0.733 | 0.515 | 1.08 | 0.757
1 | 80 | 0.354 | 0.247 | 0.594 | 0.416 | 0.945 | 0.663 | 1.44 | 1.01 | 2.11 | 1.48
1 1/4 | 80 | 0.764 | 0.534 | 1.28 | 0.896 | 2.03 | 1.43 | 3.08 | 2.17 | 4.52 | 3.19
1 1/2 | 80 | 1.17 | 0.817 | 1.95 | 1.37 | 3.1 | 2.18 | 4.7 | 3.31 | 6.89 | 4.86
2 | 40 | 2.72 | 1.91 | 4.55 | 3.19 | 7.2 | 5.07 | 10.9 | 7.71 | 16 | 11.3
2 1/2 | 40 | 4.35 | 3.05 | 7.25 | 5.1 | 11.5 | 8.1 | 17.4 | 12.3 | 25.5 | 18
3 | 40 | 7.7 | 5.41 | 12.8 | 9.04 | 20.3 | 14.3 | 30.8 | 21.7 | 45.1 | 31.8
4 | 40 | 15.7 | 11.1 | 26.2 | 18.4 | 41.4 | 29.2 | 62.7 | 44.3 | 91.8 | 64.8
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.19 | 1.11 | 1.04 | 0.96 | 0.88 | 0.8 | 0.71
SI
Table 18 Suction Line Capacities in Tons for Refrigerant 454C (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 2.17 kPa | Dp = 1.09 kPa | Dp = 3.11 kPa | Dp = 1.56 kPa | Dp = 4.31 kPa | Dp = 2.16 kPa | Dp = 6.65 kPa | Dp = 3.33 kPa | Dp = 8.60 kPa | Dp = 4.32 kPa
3/8 (10) |  | --- | --- | 0.11 | --- | 0.173 | 0.117 | 0.319 | 0.217 | 0.46 | 0.313
1/2 (13) |  | 0.167 | 0.113 | 0.274 | 0.186 | 0.431 | 0.293 | 0.789 | 0.538 | 1.14 | 0.775
5/8 (16) |  | 0.304 | 0.206 | 0.5 | 0.34 | 0.784 | 0.534 | 1.43 | 0.978 | 2.06 | 1.41
3/4 (19) |  | 0.522 | 0.355 | 0.856 | 0.583 | 1.34 | 0.914 | 2.45 | 1.67 | 3.51 | 2.4
7/8 (22) |  | 0.812 | 0.552 | 1.33 | 0.906 | 2.08 | 1.42 | 3.79 | 2.59 | 5.43 | 3.73
1 1/8 (29) |  | 1.66 | 1.13 | 2.71 | 1.85 | 4.23 | 2.9 | 7.69 | 5.28 | 11 | 7.57
1 3/8 (35) |  | 2.91 | 1.99 | 4.75 | 3.25 | 7.41 | 5.07 | 13.4 | 9.23 | 19.2 | 13.2
1 5/8 (41) |  | 4.63 | 3.16 | 7.54 | 5.16 | 11.7 | 8.05 | 21.3 | 14.6 | 30.4 | 20.9
2 1/8 (54) |  | 9.66 | 6.61 | 15.7 | 10.8 | 24.4 | 16.8 | 44.1 | 30.4 | 62.9 | 43.5
2 5/8 (67) |  | 17.2 | 11.8 | 27.9 | 19.1 | 43.3 | 29.8 | 78 | 53.9 | 111 | 76.9
3 1/8 (79) |  | 27.5 | 18.9 | 44.6 | 30.7 | 69.1 | 47.6 | 125 | 86.1 | 177 | 123
3 5/8 (92) |  | 40.9 | 28.1 | 66.4 | 45.7 | 103 | 71 | 185 | 128 | 263 | 183
4 1/8 (105) |  | 53.9 | 39.8 | 87.8 | 64.6 | 138 | 100 | 253 | 181 | 368 | 258
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.135 | --- | 0.217 | 0.151 | 0.333 | 0.232 | 0.591 | 0.414 | 0.834 | 0.585
1/2 (13) | 80 | 0.268 | 0.186 | 0.43 | 0.299 | 0.659 | 0.46 | 1.17 | 0.818 | 1.64 | 1.15
3/4 (19) | 80 | 0.609 | 0.424 | 0.974 | 0.68 | 1.49 | 1.04 | 2.63 | 1.85 | 3.71 | 2.61
1 (25) | 80 | 1.2 | 0.836 | 1.92 | 1.34 | 2.93 | 2.05 | 5.16 | 3.63 | 7.27 | 5.12
1 1/4 (32) | 80 | 2.59 | 1.81 | 4.12 | 2.89 | 6.29 | 4.42 | 11.1 | 7.8 | 15.6 | 11
1 1/2 (38) | 80 | 3.96 | 2.77 | 6.3 | 4.42 | 9.6 | 6.75 | 16.9 | 11.9 | 23.8 | 16.8
2 (51) | 40 | 9.23 | 6.47 | 14.7 | 10.3 | 22.3 | 15.7 | 39.3 | 27.7 | 55.2 | 38.9
2 1/2 (64) | 40 | 14.7 | 10.3 | 23.4 | 16.5 | 35.6 | 25.1 | 62.6 | 44.2 | 88 | 62.1
3 (76) | 40 | 26.1 | 18.3 | 41.4 | 29.2 | 63 | 44.4 | 111 | 78.1 | 155 | 110
4 (102) | 40 | 53.3 | 37.5 | 84.5 | 59.5 | 128 | 90.6 | 226 | 159 | 317 | 224
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.2 | 1.14 | 1.07 | 0.93 | 0.86 | 0.78 | 0.7

## Table 19
I-P
Table 19 Suction Line Capacities in Tons for Refrigerant 455A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.37 psi | Dp = 0.19 psi | Dp = 0.56 psi | Dp = 0.28 psi | Dp = 0.79 psi | Dp = 0.40 psi | Dp = 1.09 psi | Dp = 0.55 psi | Dp = 1.45 psi | Dp = 0.73 psi
3/8 |  | --- | --- | --- | --- | --- | --- | --- | --- | 0.143 | ---
1/2 |  | --- | --- | --- | --- | 0.151 | 0.103 | 0.235 | 0.16 | 0.353 | 0.241
5/8 |  | --- | --- | 0.168 | 0.114 | 0.274 | 0.187 | 0.427 | 0.292 | 0.64 | 0.438
3/4 |  | 0.167 | 0.114 | 0.288 | 0.196 | 0.469 | 0.32 | 0.729 | 0.499 | 1.09 | 0.748
7/8 |  | 0.26 | 0.177 | 0.447 | 0.305 | 0.727 | 0.497 | 1.13 | 0.774 | 1.69 | 1.16
1 1/8 |  | 0.53 | 0.362 | 0.91 | 0.622 | 1.48 | 1.01 | 2.29 | 1.57 | 3.42 | 2.35
1 3/8 |  | 0.93 | 0.635 | 1.59 | 1.09 | 2.58 | 1.77 | 4 | 2.75 | 5.96 | 4.11
1 5/8 |  | 1.48 | 1.01 | 2.53 | 1.73 | 4.09 | 2.81 | 6.33 | 4.36 | 9.43 | 6.5
2 1/8 |  | 3.08 | 2.11 | 5.26 | 3.62 | 8.51 | 5.86 | 13.1 | 9.07 | 19.5 | 13.5
2 5/8 |  | 5.47 | 3.76 | 9.33 | 6.42 | 15.1 | 10.4 | 23.2 | 16.1 | 34.5 | 23.9
3 1/8 |  | 8.77 | 6.02 | 14.9 | 10.3 | 24.1 | 16.6 | 37.1 | 25.6 | 55 | 38.1
3 5/8 |  | 12.5 | 8.99 | 21.5 | 15.3 | 35.1 | 24.7 | 55 | 38.2 | 81.7 | 56.7
4 1/8 |  | 16.3 | 12.7 | 27.9 | 21.6 | 45.6 | 34.9 | 71.4 | 53.9 | 108 | 79.9
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.115 | --- | 0.176 | 0.123 | 0.258 | 0.181
1/2 | 80 | --- | --- | 0.143 | 0.1 | 0.228 | 0.16 | 0.347 | 0.243 | 0.509 | 0.358
3/4 | 80 | 0.194 | 0.135 | 0.325 | 0.227 | 0.516 | 0.361 | 0.783 | 0.55 | 1.15 | 0.807
1 | 80 | 0.382 | 0.266 | 0.638 | 0.447 | 1.01 | 0.71 | 1.54 | 1.08 | 2.25 | 1.58
1 1/4 | 80 | 0.823 | 0.575 | 1.37 | 0.963 | 2.17 | 1.53 | 3.3 | 2.32 | 4.82 | 3.4
1 1/2 | 80 | 1.26 | 0.88 | 2.1 | 1.47 | 3.32 | 2.33 | 5.03 | 3.54 | 7.35 | 5.18
2 | 40 | 2.93 | 2.06 | 4.88 | 3.43 | 7.71 | 5.43 | 11.7 | 8.24 | 17.1 | 12
2 1/2 | 40 | 4.68 | 3.29 | 7.79 | 5.48 | 12.3 | 8.67 | 18.6 | 13.1 | 27.2 | 19.2
3 | 40 | 8.29 | 5.83 | 13.8 | 9.7 | 21.8 | 15.3 | 32.9 | 23.2 | 48.1 | 34
4 | 40 | 16.9 | 11.9 | 28.1 | 19.8 | 44.3 | 31.3 | 67 | 47.3 | 97.9 | 69.2
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.19 | 1.11 | 1.04 | 0.96 | 0.88 | 0.8 | 0.71
SI
Table 19 Suction Line Capacities in Tons for Refrigerant 455A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 2.31 kPa | Dp = 1.16 kPa | Dp = 3.32 kPa | Dp = 1.67 kPa | Dp = 4.60 kPa | Dp = 2.31 kPa | Dp = 7.09 kPa | Dp = 3.56 kPa | Dp = 9.18 kPa | Dp = 4.60 kPa
3/8 (10) |  | --- | --- | 0.119 | --- | 0.186 | 0.126 | 0.342 | 0.232 | 0.492 | 0.335
1/2 (13) |  | 0.18 | 0.122 | 0.295 | 0.2 | 0.463 | 0.315 | 0.846 | 0.576 | 1.21 | 0.829
5/8 (16) |  | 0.329 | 0.223 | 0.539 | 0.366 | 0.843 | 0.574 | 1.54 | 1.05 | 2.2 | 1.51
3/4 (19) |  | 0.564 | 0.383 | 0.922 | 0.628 | 1.44 | 0.983 | 2.62 | 1.79 | 3.75 | 2.57
7/8 (22) |  | 0.877 | 0.596 | 1.43 | 0.976 | 2.24 | 1.53 | 4.06 | 2.78 | 5.8 | 3.98
1 1/8 (29) |  | 1.79 | 1.22 | 2.92 | 1.99 | 4.55 | 3.11 | 8.24 | 5.65 | 11.8 | 8.09
1 3/8 (35) |  | 3.14 | 2.15 | 5.11 | 3.5 | 7.95 | 5.45 | 14.4 | 9.88 | 20.5 | 14.1
1 5/8 (41) |  | 4.99 | 3.41 | 8.11 | 5.56 | 12.6 | 8.65 | 22.8 | 15.7 | 32.4 | 22.4
2 1/8 (54) |  | 10.4 | 7.14 | 16.9 | 11.6 | 26.2 | 18 | 47.2 | 32.6 | 67.2 | 46.4
2 5/8 (67) |  | 18.5 | 12.7 | 30 | 20.6 | 46.4 | 32 | 83.5 | 57.7 | 119 | 82.2
3 1/8 (79) |  | 29.6 | 20.4 | 48 | 33 | 74.2 | 51.2 | 133 | 92.1 | 189 | 131
3 5/8 (92) |  | 43.8 | 30.4 | 71.2 | 49.2 | 110 | 76.2 | 198 | 137 | 281 | 195
4 1/8 (105) |  | 56.9 | 43 | 92.6 | 69.5 | 145 | 108 | 266 | 193 | 385 | 275
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.146 | 0.101 | 0.233 | 0.162 | 0.357 | 0.249 | 0.632 | 0.442 | 0.89 | 0.624
1/2 (13) | 80 | 0.289 | 0.2 | 0.462 | 0.322 | 0.707 | 0.494 | 1.25 | 0.874 | 1.75 | 1.23
3/4 (19) | 80 | 0.656 | 0.457 | 1.05 | 0.731 | 1.6 | 1.12 | 2.81 | 1.98 | 3.95 | 2.78
1 (25) | 80 | 1.29 | 0.901 | 2.06 | 1.44 | 3.14 | 2.2 | 5.52 | 3.88 | 7.75 | 5.46
1 1/4 (32) | 80 | 2.79 | 1.95 | 4.43 | 3.1 | 6.74 | 4.74 | 11.8 | 8.34 | 16.6 | 11.7
1 1/2 (38) | 80 | 4.26 | 2.98 | 6.76 | 4.74 | 10.3 | 7.23 | 18.1 | 12.7 | 25.3 | 17.9
2 (51) | 40 | 9.94 | 6.96 | 15.8 | 11.1 | 23.9 | 16.8 | 42 | 29.6 | 58.9 | 41.5
2 1/2 (64) | 40 | 15.9 | 11.1 | 25.2 | 17.7 | 38.2 | 26.9 | 66.9 | 47.2 | 93.8 | 66.2
3 (76) | 40 | 28.1 | 19.7 | 44.5 | 31.3 | 67.5 | 47.6 | 118 | 83.5 | 166 | 117
4 (102) | 40 | 57.4 | 40.4 | 90.8 | 63.9 | 138 | 97.1 | 241 | 170 | 338 | 238
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.2 | 1.13 | 1.07 | 0.93 | 0.86 | 0.78 | 0.71

## Table 20
I-P
Table 20 Suction Line Capacities in Tons for Refrigerant 457A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | -40 |  | -20 |  | 0 |  | 20 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.32 psi | Dp = 0.16 psi | Dp = 0.47 psi | Dp = 0.24 psi | Dp = 0.68 psi | Dp = 0.34 psi | Dp = 0.94 psi | Dp = 0.47 psi | Dp = 1.26 psi | Dp = 0.63 psi
3/8 |  | --- | --- | --- | --- | --- | --- | --- | --- | 0.13 | ---
1/2 |  | --- | --- | --- | --- | 0.136 | --- | 0.213 | 0.145 | 0.32 | 0.219
5/8 |  | --- | --- | 0.151 | 0.103 | 0.248 | 0.169 | 0.387 | 0.264 | 0.581 | 0.397
3/4 |  | 0.15 | 0.102 | 0.259 | 0.176 | 0.424 | 0.289 | 0.661 | 0.452 | 0.991 | 0.679
7/8 |  | 0.233 | 0.159 | 0.403 | 0.274 | 0.657 | 0.449 | 1.02 | 0.701 | 1.53 | 1.05
1 1/8 |  | 0.477 | 0.325 | 0.821 | 0.561 | 1.34 | 0.916 | 2.08 | 1.43 | 3.11 | 2.14
1 3/8 |  | 0.836 | 0.571 | 1.44 | 0.984 | 2.34 | 1.6 | 3.63 | 2.5 | 5.42 | 3.73
1 5/8 |  | 1.33 | 0.908 | 2.28 | 1.56 | 3.71 | 2.54 | 5.75 | 3.96 | 8.58 | 5.91
2 1/8 |  | 2.78 | 1.9 | 4.76 | 3.26 | 7.71 | 5.3 | 11.9 | 8.23 | 17.8 | 12.3
2 5/8 |  | 4.93 | 3.38 | 8.44 | 5.8 | 13.7 | 9.41 | 21.1 | 14.6 | 31.4 | 21.7
3 1/8 |  | 7.9 | 5.42 | 13.5 | 9.29 | 21.8 | 15.1 | 33.7 | 23.3 | 50.1 | 34.7
3 5/8 |  | 11.4 | 8.09 | 19.5 | 13.8 | 31.9 | 22.4 | 50.1 | 34.7 | 74.5 | 51.6
4 1/8 |  | 14.8 | 11.5 | 25.4 | 19.6 | 41.5 | 31.7 | 65.1 | 49 | 98.8 | 72.8
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.105 | --- | 0.161 | 0.112 | 0.236 | 0.166
1/2 | 80 | --- | --- | 0.13 | --- | 0.208 | 0.145 | 0.317 | 0.222 | 0.466 | 0.327
3/4 | 80 | 0.176 | 0.122 | 0.295 | 0.206 | 0.47 | 0.329 | 0.716 | 0.503 | 1.05 | 0.739
1 | 80 | 0.346 | 0.241 | 0.581 | 0.406 | 0.924 | 0.648 | 1.41 | 0.988 | 2.06 | 1.45
1 1/4 | 80 | 0.747 | 0.521 | 1.25 | 0.876 | 1.99 | 1.39 | 3.02 | 2.12 | 4.42 | 3.11
1 1/2 | 80 | 1.14 | 0.798 | 1.91 | 1.34 | 3.03 | 2.13 | 4.6 | 3.24 | 6.74 | 4.75
2 | 40 | 2.66 | 1.87 | 4.45 | 3.12 | 7.05 | 4.96 | 10.7 | 7.54 | 15.7 | 11
2 1/2 | 40 | 4.26 | 2.98 | 7.1 | 4.99 | 11.2 | 7.92 | 17.1 | 12 | 25 | 17.6
3 | 40 | 7.54 | 5.29 | 12.6 | 8.84 | 19.9 | 14 | 30.2 | 21.3 | 44.1 | 31.1
4 | 40 | 15.4 | 10.8 | 25.6 | 18.1 | 40.5 | 28.6 | 61.4 | 43.4 | 89.8 | 63.4
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.17 | 1.1 | 1.04 | 0.96 | 0.89 | 0.82 | 0.74
SI
Table 20 Suction Line Capacities in Tons for Refrigerant 457A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -40 |  | -30 |  | -20 |  | -5 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 1.97 kPa | Dp = 0.99 kPa | Dp = 2.84 kPa | Dp = 1.42 kPa | Dp = 3.94 kPa | Dp = 1.98 kPa | Dp = 6.10 kPa | Dp = 3.06 kPa | Dp = 7.92 kPa | Dp = 3.97 kPa
3/8 (10) |  | --- | --- | 0.106 | --- | 0.168 | 0.113 | 0.309 | 0.21 | 0.445 | 0.303
1/2 (13) |  | 0.161 | 0.109 | 0.265 | 0.18 | 0.417 | 0.283 | 0.765 | 0.521 | 1.1 | 0.751
5/8 (16) |  | 0.294 | 0.199 | 0.484 | 0.329 | 0.76 | 0.517 | 1.39 | 0.948 | 2 | 1.36
3/4 (19) |  | 0.506 | 0.343 | 0.83 | 0.564 | 1.3 | 0.886 | 2.37 | 1.62 | 3.41 | 2.33
7/8 (22) |  | 0.787 | 0.535 | 1.29 | 0.878 | 2.02 | 1.38 | 3.68 | 2.52 | 5.27 | 3.61
1 1/8 (29) |  | 1.61 | 1.1 | 2.63 | 1.8 | 4.11 | 2.81 | 7.47 | 5.12 | 10.7 | 7.34
1 3/8 (35) |  | 2.82 | 1.93 | 4.61 | 3.15 | 7.19 | 4.92 | 13 | 8.96 | 18.7 | 12.8
1 5/8 (41) |  | 4.49 | 3.07 | 7.32 | 5.01 | 11.4 | 7.82 | 20.7 | 14.2 | 29.5 | 20.3
2 1/8 (54) |  | 9.37 | 6.42 | 15.3 | 10.5 | 23.7 | 16.3 | 42.9 | 29.5 | 61.2 | 42.2
2 5/8 (67) |  | 16.7 | 11.4 | 27.1 | 18.6 | 42.1 | 28.9 | 75.9 | 52.3 | 108 | 74.7
3 1/8 (79) |  | 26.7 | 18.3 | 43.3 | 29.8 | 67.2 | 46.3 | 121 | 83.7 | 173 | 119
3 5/8 (92) |  | 39.7 | 27.3 | 64.5 | 44.4 | 100 | 69 | 180 | 125 | 256 | 178
4 1/8 (105) |  | 51.6 | 38.7 | 84.1 | 62.8 | 132 | 97.5 | 242 | 176 | 351 | 250
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.132 | --- | 0.212 | 0.147 | 0.325 | 0.226 | 0.577 | 0.404 | 0.814 | 0.571
1/2 (13) | 80 | 0.261 | 0.181 | 0.42 | 0.292 | 0.643 | 0.449 | 1.14 | 0.798 | 1.61 | 1.13
3/4 (19) | 80 | 0.594 | 0.413 | 0.951 | 0.663 | 1.46 | 1.02 | 2.57 | 1.81 | 3.62 | 2.55
1 (25) | 80 | 1.17 | 0.815 | 1.87 | 1.31 | 2.86 | 2 | 5.05 | 3.55 | 7.1 | 5
1 1/4 (32) | 80 | 2.53 | 1.76 | 4.03 | 2.82 | 6.15 | 4.32 | 10.8 | 7.62 | 15.2 | 10.7
1 1/2 (38) | 80 | 3.86 | 2.7 | 6.16 | 4.31 | 9.39 | 6.59 | 16.5 | 11.6 | 23.2 | 16.4
2 (51) | 40 | 9.02 | 6.32 | 14.3 | 10.1 | 21.9 | 15.4 | 38.4 | 27.1 | 54 | 38.1
2 1/2 (64) | 40 | 14.4 | 10.1 | 22.9 | 16.1 | 34.9 | 24.5 | 61.3 | 43.2 | 86 | 60.7
3 (76) | 40 | 25.5 | 17.9 | 40.6 | 28.5 | 61.7 | 43.4 | 108 | 76.4 | 152 | 107
4 (102) | 40 | 52.2 | 36.6 | 82.7 | 58.2 | 126 | 88.6 | 221 | 156 | 310 | 219
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.18 | 1.12 | 1.06 | 0.94 | 0.87 | 0.8 | 0.73

## Table 21
I-P
Table 21 Suction Line Capacities in Tons for Refrigerant 516A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °F
Type L, |  | 0 |  | 10 |  | 20 |  | 30 |  | 40
Copper, |  | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F | Dt = 1°F | Dt = 0.5°F
OD, in |  | Dp = 0.53 psi | Dp = 0.26 psi | Dp = 0.62 psi | Dp = 0.31 psi | Dp = 0.73 psi | Dp = 0.37 psi | Dp = 0.85 psi | Dp = 0.43 psi | Dp = 0.98 psi | Dp = 0.49 psi
3/8 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
1/2 |  | --- | --- | 0.124 | --- | 0.156 | 0.106 | 0.193 | 0.131 | 0.237 | 0.162
5/8 |  | 0.178 | 0.121 | 0.226 | 0.154 | 0.283 | 0.193 | 0.351 | 0.239 | 0.43 | 0.294
3/4 |  | 0.305 | 0.208 | 0.386 | 0.263 | 0.483 | 0.33 | 0.599 | 0.409 | 0.734 | 0.503
7/8 |  | 0.473 | 0.323 | 0.599 | 0.409 | 0.749 | 0.512 | 0.927 | 0.635 | 1.14 | 0.779
1 1/8 |  | 0.964 | 0.659 | 1.22 | 0.834 | 1.52 | 1.04 | 1.88 | 1.29 | 2.31 | 1.58
1 3/8 |  | 1.69 | 1.16 | 2.13 | 1.46 | 2.66 | 1.83 | 3.29 | 2.26 | 4.03 | 2.77
1 5/8 |  | 2.68 | 1.83 | 3.38 | 2.32 | 4.22 | 2.9 | 5.21 | 3.58 | 6.38 | 4.39
2 1/8 |  | 5.57 | 3.83 | 7.03 | 4.83 | 8.76 | 6.03 | 10.8 | 7.45 | 13.2 | 9.13
2 5/8 |  | 9.87 | 6.79 | 12.4 | 8.57 | 15.5 | 10.7 | 19.1 | 13.2 | 23.4 | 16.2
3 1/8 |  | 15.8 | 10.9 | 19.9 | 13.7 | 24.8 | 17.1 | 30.6 | 21.1 | 37.3 | 25.8
3 5/8 |  | 23.5 | 16.2 | 29.6 | 20.4 | 36.9 | 25.5 | 45.4 | 31.4 | 55.5 | 38.4
4 1/8 |  | 32.5 | 22.9 | 41.2 | 28.8 | 51.7 | 35.9 | 64.1 | 44.3 | 78.3 | 54.2
Steel
IPS | SCH
3/8 | 80 | --- | --- | --- | --- | 0.119 | --- | 0.146 | 0.102 | 0.177 | 0.124
1/2 | 80 | 0.151 | 0.106 | 0.189 | 0.132 | 0.234 | 0.164 | 0.287 | 0.201 | 0.349 | 0.245
3/4 | 80 | 0.342 | 0.239 | 0.428 | 0.3 | 0.53 | 0.372 | 0.649 | 0.456 | 0.788 | 0.554
1 | 80 | 0.673 | 0.471 | 0.841 | 0.59 | 1.04 | 0.73 | 1.27 | 0.895 | 1.55 | 1.09
1 1/4 | 80 | 1.45 | 1.02 | 1.81 | 1.27 | 2.23 | 1.57 | 2.73 | 1.92 | 3.32 | 2.33
1 1/2 | 80 | 2.21 | 1.55 | 2.76 | 1.94 | 3.41 | 2.4 | 4.17 | 2.94 | 5.06 | 3.56
2 | 40 | 5.14 | 3.62 | 6.42 | 4.52 | 7.92 | 5.58 | 9.69 | 6.83 | 11.8 | 8.29
2 1/2 | 40 | 8.21 | 5.77 | 10.2 | 7.21 | 12.6 | 8.91 | 15.5 | 10.9 | 18.7 | 13.2
3 | 40 | 14.5 | 10.2 | 18.1 | 12.8 | 22.3 | 15.8 | 27.3 | 19.3 | 33.1 | 23.4
4 | 40 | 29.6 | 20.9 | 36.9 | 26 | 45.5 | 32.1 | 55.7 | 39.3 | 67.4 | 47.6
Notes:
1. Table capacities are in tons of refrigeration. Maximum veloxity = 3000 fpm. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, psi per 100 ft equivalent length.
Dt = change in saturation temperature corresponding to Dp, °F per 100 ft equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 105°F liquid temperature entering the expension device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a 20°F evaporator temperature, and are suitable in the range of 0°F to 40°F.
Liquid Temperature, °F
|  |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
| Suction Line |  | 1.17 | 1.1 | 1.04 | 0.96 | 0.89 | 0.82 | 0.74
SI
Table 21 Suction Line Capacities in Tons for Refrigerant 516A (Single- or High-Stage Applications)
Line Size |  | Saturated Suction Temperature, °C
Type L, |  | -15 |  | -10 |  | -5 |  | 0 |  | 5
Copper, |  | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K | Dt = 0.5 K | Dt = 0.25 K
OD, in (mm) |  | Dp = 3.56 kPa | Dp = 1.79 kPa | Dp = 4.12 kPa | Dp = 2.07 kPa | Dp = 4.74 kPa | Dp = 2.38 kPa | Dp = 5.42 kPa | Dp = 2.72 kPa | Dp = 6.16 kPa | Dp = 3.09 kPa
3/8 (10) |  | 0.149 | 0.101 | 0.184 | 0.125 | 0.226 | 0.153 | 0.274 | 0.186 | 0.329 | 0.224
1/2 (13) |  | 0.372 | 0.252 | 0.458 | 0.311 | 0.56 | 0.381 | 0.678 | 0.462 | 0.815 | 0.556
5/8 (16) |  | 0.677 | 0.461 | 0.834 | 0.568 | 1.02 | 0.694 | 1.23 | 0.841 | 1.48 | 1.01
3/4 (19) |  | 1.16 | 0.79 | 1.43 | 0.973 | 1.74 | 1.19 | 2.1 | 1.44 | 2.53 | 1.73
7/8 (22) |  | 1.8 | 1.23 | 2.21 | 1.51 | 2.7 | 1.84 | 3.26 | 2.23 | 3.91 | 2.68
1 1/8 (29) |  | 3.66 | 2.5 | 4.5 | 3.08 | 5.48 | 3.76 | 6.62 | 4.54 | 7.94 | 5.45
1 3/8 (35) |  | 6.41 | 4.39 | 7.87 | 5.39 | 9.58 | 6.57 | 11.6 | 7.94 | 13.9 | 9.53
1 5/8 (41) |  | 10.2 | 6.97 | 12.5 | 8.56 | 15.2 | 10.4 | 18.3 | 12.6 | 21.9 | 15.1
2 1/8 (54) |  | 21.2 | 14.5 | 25.9 | 17.8 | 31.5 | 21.7 | 38.1 | 26.2 | 45.6 | 31.4
2 5/8 (67) |  | 37.5 | 25.8 | 46 | 31.6 | 55.8 | 38.5 | 67.3 | 46.4 | 80.6 | 55.6
3 1/8 (79) |  | 59.9 | 41.3 | 73.4 | 50.6 | 89.2 | 61.5 | 107 | 74.2 | 129 | 88.8
3 5/8 (92) |  | 89.2 | 61.5 | 109 | 75.4 | 133 | 91.6 | 160 | 110 | 191 | 132
4 1/8 (105) |  | 126 | 86.9 | 154 | 106 | 187 | 129 | 225 | 156 | 270 | 187
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 0.29 | 0.202 | 0.353 | 0.247 | 0.427 | 0.298 | 0.512 | 0.358 | 0.61 | 0.427
1/2 (13) | 80 | 0.574 | 0.4 | 0.699 | 0.488 | 0.844 | 0.591 | 1.01 | 0.709 | 1.2 | 0.844
3/4 (19) | 80 | 1.3 | 0.908 | 1.58 | 1.11 | 1.91 | 1.34 | 2.28 | 1.6 | 2.72 | 1.91
1 (25) | 80 | 2.55 | 1.79 | 3.1 | 2.18 | 3.74 | 2.63 | 4.48 | 3.15 | 5.33 | 3.75
1 1/4 (32) | 80 | 5.48 | 3.85 | 6.67 | 4.68 | 8.04 | 5.65 | 9.62 | 6.77 | 11.4 | 8.05
1 1/2 (38) | 80 | 8.37 | 5.88 | 10.2 | 7.15 | 12.3 | 8.63 | 14.7 | 10.3 | 17.4 | 12.3
2 (51) | 40 | 19.5 | 13.7 | 23.7 | 16.7 | 28.5 | 20.1 | 34.1 | 24 | 40.5 | 28.6
2 1/2 (64) | 40 | 31.1 | 21.9 | 37.8 | 26.6 | 45.5 | 32.1 | 54.4 | 38.4 | 64.6 | 45.6
3 (76) | 40 | 55 | 38.7 | 66.8 | 47.1 | 80.4 | 56.7 | 96.2 | 67.8 | 114 | 80.6
4 (102) | 40 | 112 | 79 | 136 | 96 | 164 | 116 | 196 | 138 | 233 | 164
Notes:
1. Table capacities are in kilowatts of refrigeration. Maximum veloxity = 15 m/s. Suction refrigerant state is at saturation.
Dp = pressure drop from line friction, kPa per 30 meters equivalent length.
Dt = change in saturation temperature corresponding to Dp, K per 30 meters equivalent length.
2. Line capacity for other saturation temperatures Dt and equivalent lengths Le
3. Saturation temperature Dt for other capacities and equivalent lengths Le
4. Refrigerant thermodynamic and thermophysical properties calculated using NIST RefProp v10.0. Refrigerant flow rates calculated using the Darcy-Weisbach and Colebrook equations.
5. Table capacities based on 40°C liquid temperature entering the expansion device. Multiply capacities by the following correction factors for other liquid temperatures. Correction factors based on a -5°C evaporator temperature, and are suitable in the range of -15°C to 5°C.
Liquid Temperature, °C
|  |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
| Suction Line |  | 1.18 | 1.12 | 1.06 | 0.94 | 0.87 | 0.81 | 0.74

## Example 2
I-P
Example 2. An R-454B air conditioning system using copper pipe operates at
40°F evaporator and 100°F condensing. Capacity is 20 tons, and the
suction line has 50 ft of straight pipe with six long-radius elbows. Determine the
suction line size and pressure drop equivalent (in temperature difference).
Solution: From Table 4, the rating for the 1-5/8" OD suction line at a 2°F loss per 100 ft
equivalent length is 25.1 tons at 40°F evaporator and 105°F condensing. Use
Note 5, Table 4, to determine capacity at 40°F evaporator and 100°F condensing:
Actual 1-5/8" OD line capacity | = | 25.1 x 1.03 | = | 25.9 tons
Straight pipe length |  |  | = | 50 ft
Six long-radius elbows
(Table 22, using 1-1/2" OD size) = |  | 6 x 2.6 | = | 15.6 ft
Total equivalent length |  |  |  | 65.6 ft
Use the equation in Note 3 of Table 4 to compute actual temperature difference.
Dt | = | 2.0(65.6/100)(20.0/25.9)1.8 = |  | 0.82°F
|  |  | or | 1.71 psi
SI
Example 2. An R-454B air conditioning system using copper pipe operates at
5°C evaporator and 35°C condensing. Capacity is 105 kW, and the
suction line has 15 m of straight pipe with six long-radius elbows. Determine the
suction line size and pressure drop equivalent (in temperature difference).
Solution: From Table 4, the rating for the 41 mm OD suction line at a 1 K loss per 30 m
equivalent length is 86.0 kW at 5°C evaporator and 40°C condensing. Use
Note 5, Table 4, to determine capacity at 5°C evaporator and 35°C condensing:
Actual 41 mm OD line capacity | = | 86.0 x 1.05 | = | 90.3 kW
Straight pipe length |  |  | = | 15 m
Six long-radius elbows
(Table 22, using 38 mm OD size) = |  | 6 x 0.8 | = | 4.8 m
Total equivalent length |  |  |  | 19.8 m
Use the equation in Note 3 of Table 4 to compute actual temperature difference.
Dt | = | 1.0(19.8/30)(105.0/90.3)1.8 = |  | 0.87 K
|  |  | or | 23 kPa

## Table 22
I-P
Table 22 Fitting Losses in Equivalent Feet of Pipe (Screwed, Welded, Flanged, Flared and Brazed Connections)
Nominal
Pipe or
Tube Size,
in
3/8 | 1.4 | 0.9 | 2.3 | 0.7 | 1.1 | 2.3 | 2.7 | 0.9 | 1.2 | 1.4
1/2 | 1.6 | 1 | 2.5 | 0.8 | 1.3 | 2.5 | 3 | 1 | 1.4 | 1.6
3/4 | 2 | 1.4 | 3.2 | 0.9 | 1.6 | 3.2 | 4 | 1.4 | 1.9 | 2
1 | 2.6 | 1.7 | 4.1 | 1.3 | 2.1 | 4.1 | 5 | 1.7 | 2.2 | 2.6
1 1/4 | 3.3 | 2.3 | 5.6 | 1.7 | 3 | 5.6 | 7 | 2.3 | 3.1 | 3.3
1 1/2 | 4 | 2.6 | 6.3 | 2.1 | 3.4 | 6.3 | 8 | 2.6 | 3.7 | 4
2 | 5 | 3.3 | 8.2 | 2.6 | 4.5 | 8.2 | 10 | 3.3 | 4.7 | 5
2 1/2 | 6 | 4.1 | 10 | 3.2 | 5.2 | 10 | 12 | 4.1 | 5.6 | 6
3 | 7.5 | 5 | 12 | 4 | 6.4 | 12 | 15 | 5 | 7 | 7.5
3 1/2 | 9 | 5.9 | 15 | 4.7 | 7.3 | 15 | 18 | 5.9 | 8 | 9
4 | 10 | 6.7 | 17 | 5.2 | 8.5 | 17 | 21 | 6.7 | 9 | 10
5 | 13 | 8.2 | 21 | 6.5 | 11 | 21 | 25 | 8.2 | 12 | 13
6 | 16 | 10 | 25 | 7.9 | 13 | 25 | 30 | 10 | 14 | 16
8 | 20 | 13 | — | 10 | — | 33 | 40 | 13 | 18 | 20
10 | 25 | 16 | — | 13 | — | 42 | 50 | 16 | 23 | 25
12 | 30 | 19 | — | 16 | — | 50 | 60 | 19 | 26 | 30
14 | 34 | 23 | — | 18 | — | 55 | 68 | 23 | 30 | 34
16 | 38 | 26 | — | 20 | — | 62 | 78 | 26 | 35 | 38
18 | 42 | 29 | — | 23 | — | 70 | 85 | 29 | 40 | 42
20 | 50 | 33 | — | 26 | — | 81 | 100 | 33 | 44 | 50
24 | 60 | 40 | — | 30 | — | 94 | 115 | 40 | 50 | 60
aR/D approximately equal to 1.
bR/D approximately equal to 1.5.
SI
Table 22 Fitting Losses in Equivalent Meters of Pipe (Screwed, Welded, Flanged, Flared and Brazed Connections)
Nominal
Pipe or
Tube Size,
in (mm)
3/8 (10) | 0.4 | 0.3 | 0.7 | 0.2 | 0.3 | 0.7 | 0.8 | 0.3 | 0.4 | 0.4
1/2 (13) | 0.5 | 0.3 | 0.8 | 0.2 | 0.4 | 0.8 | 0.9 | 0.3 | 0.4 | 0.5
3/4 (19) | 0.6 | 0.4 | 1 | 0.3 | 0.5 | 1 | 1.2 | 0.4 | 0.6 | 0.6
1 (25) | 0.8 | 0.5 | 1.2 | 0.4 | 0.6 | 1.2 | 1.5 | 0.5 | 0.7 | 0.8
1 1/4 (32) | 1 | 0.7 | 1.7 | 0.5 | 0.9 | 1.7 | 2.1 | 0.7 | 0.9 | 1
1 1/2 (38) | 1.2 | 0.8 | 1.9 | 0.6 | 1 | 1.9 | 2.4 | 0.8 | 1.1 | 1.2
2 (51) | 1.5 | 1 | 2.5 | 0.8 | 1.4 | 2.5 | 3 | 1 | 1.4 | 1.5
2 1/2 (64) | 1.8 | 1.2 | 3 | 1 | 1.6 | 3 | 3.7 | 1.2 | 1.7 | 1.8
3 (76) | 2.3 | 1.5 | 3.7 | 1.2 | 2 | 3.7 | 4.6 | 1.5 | 2.1 | 2.3
3 1/2 (89) | 2.7 | 1.8 | 4.6 | 1.4 | 2.2 | 4.6 | 5.5 | 1.8 | 2.4 | 2.7
4 (102) | 3 | 2 | 5.2 | 1.6 | 2.6 | 5.2 | 6.4 | 2 | 2.7 | 3
5 (127) | 4 | 2.5 | 6.4 | 2 | 3.4 | 6.4 | 7.6 | 2.5 | 3.7 | 4
6 (152) | 4.9 | 3 | 7.6 | 2.4 | 4 | 7.6 | 9 | 3 | 4.3 | 4.9
8 (203) | 6.1 | 4 | — | 3 | — | 10 | 12 | 4 | 5.5 | 6.1
10 (254) | 7.6 | 4.9 | — | 4 | — | 13 | 15 | 4.9 | 7 | 7.6
12 (305) | 9.1 | 5.8 | — | 4.9 | — | 15 | 18 | 5.8 | 7.9 | 9.1
14 (356) | 10 | 7 | — | 5.5 | — | 17 | 21 | 7 | 9.1 | 10
16 (406) | 12 | 7.9 | — | 6.1 | — | 19 | 24 | 7.9 | 11 | 12
18 (457) | 13 | 8.8 | — | 7 | — | 21 | 26 | 8.8 | 12 | 13
20 (508) | 15 | 10 | — | 7.9 | — | 25 | 30 | 10 | 13 | 15
24 (610) | 18 | 12 | — | 9.1 | — | 29 | 35 | 12 | 15 | 18
aR/D approximately equal to 1.
bR/D approximately equal to 1.5.

## Table 23
I-P
Table 23 Special Fitting Losses in Equivalent Feet of Pipe
| Sudden Enlargement, d/D |  |  | Sudden Contraction, d/D |  |  | Sharp Edge |  | Pipe Projection
| 1/4 | 1/2 | 3/4 | 1/4 | 1/2 | 3/4 | Entrance | Exit | Entrance | Exit
Nominal
Pipe or
Tube Size,
in
3/8 | 1.4 | 0.8 | 0.3 | 0.7 | 0.5 | 0.3 | 1.5 | 0.8 | 1.5 | 1.1
1/2 | 1.8 | 1.1 | 0.4 | 0.9 | 0.7 | 0.4 | 1.8 | 1 | 1.8 | 1.5
3/4 | 2.5 | 1.5 | 0.5 | 1.2 | 1 | 0.5 | 2.8 | 1.4 | 2.8 | 2.2
1 | 3.2 | 2 | 0.7 | 1.6 | 1.2 | 0.7 | 3.7 | 1.8 | 3.7 | 2.7
1 1/4 | 4.7 | 3 | 1 | 2.3 | 1.8 | 1 | 5.3 | 2.6 | 5.3 | 4.2
1 1/2 | 5.8 | 3.6 | 1.2 | 2.9 | 2.2 | 1.2 | 6.6 | 3.3 | 6.6 | 5
2 | 8 | 4.8 | 1.6 | 4 | 3 | 1.6 | 9 | 4.4 | 9 | 6.8
2 1/2 | 10 | 6.1 | 2 | 5 | 3.8 | 2 | 12 | 5.6 | 12 | 8.7
3 | 13 | 8 | 2.6 | 6.5 | 4.9 | 2.6 | 14 | 7.2 | 14 | 11
3 1/2 | 15 | 9.2 | 3 | 7.7 | 6 | 3 | 17 | 8.5 | 17 | 13
4 | 17 | 11 | 3.8 | 9 | 6.8 | 3.8 | 20 | 10 | 20 | 16
5 | 24 | 15 | 5 | 12 | 9 | 5 | 27 | 14 | 27 | 20
6 | 29 | 22 | 6 | 15 | 11 | 6 | 33 | 19 | 33 | 25
8 | — | 25 | 8.5 | — | 15 | 8.5 | 47 | 24 | 47 | 35
10 | — | 32 | 11 | — | 20 | 11 | 60 | 29 | 60 | 46
12 | — | 41 | 13 | — | 25 | 13 | 73 | 37 | 73 | 57
14 | — | — | 16 | — | — | 16 | 86 | 45 | 86 | 66
16 | — | — | 18 | — | — | 18 | 96 | 50 | 96 | 77
18 | — | — | 20 | — | — | 20 | 115 | 58 | 115 | 90
20 | — | — | — | — | — | — | 142 | 70 | 142 | 108
24 | — | — | — | — | — | — | 163 | 83 | 163 | 130
Note: Enter table for losses at smallest diameter d.
SI
Table 23 Special Fitting Losses in Equivalent Meters of Pipe
| Sudden Enlargement, d/D |  |  | Sudden Contraction, d/D |  |  | Sharp Edge |  | Pipe Projection
| 1/4 | 1/2 | 3/4 | 1/4 | 1/2 | 3/4 | Entrance | Exit | Entrance | Exit
Nominal
Pipe or
Tube Size,
in (mm)
3/8 (10) | 0.4 | 0.2 | 0.1 | 0.2 | 0.2 | 0.1 | 0.5 | 0.2 | 0.5 | 0.3
1/2 (13) | 0.5 | 0.3 | 0.1 | 0.3 | 0.3 | 0.1 | 0.5 | 0.3 | 0.5 | 0.5
3/4 (19) | 0.8 | 0.5 | 0.2 | 0.4 | 0.3 | 0.2 | 0.9 | 0.4 | 0.9 | 0.7
1 (25) | 1 | 0.6 | 0.2 | 0.5 | 0.4 | 0.2 | 1.1 | 0.5 | 1.1 | 0.8
1 1/4 (32) | 1.4 | 0.9 | 0.3 | 0.7 | 0.5 | 0.3 | 1.6 | 0.8 | 1.6 | 1.3
1 1/2 (38) | 1.8 | 1.1 | 0.4 | 0.9 | 0.7 | 0.4 | 2 | 1 | 2 | 1.5
2 (51) | 2.4 | 1.5 | 0.5 | 1.2 | 0.9 | 0.5 | 2.7 | 1.3 | 2.7 | 2.1
2 1/2 (64) | 3 | 1.9 | 0.6 | 1.5 | 1.2 | 0.6 | 3.7 | 1.7 | 3.7 | 2.7
3 (76) | 4 | 2.4 | 0.8 | 2 | 1.5 | 0.8 | 4.3 | 2.2 | 4.3 | 3.8
3 1/2 (89) | 4.6 | 2.8 | 0.9 | 2.3 | 1.8 | 0.9 | 5.2 | 2.6 | 5.2 | 4
4 (102) | 5.2 | 3.4 | 1.2 | 2.7 | 2.1 | 1.2 | 6.1 | 3 | 6.1 | 4.9
5 (127) | 7.3 | 4.6 | 1.5 | 3.7 | 2.7 | 1.5 | 8.2 | 4.3 | 8.2 | 6.1
6 (152) | 8.8 | 6.7 | 1.8 | 4.6 | 3.4 | 1.8 | 10 | 5.8 | 10 | 7.6
8 (203) | — | 7.6 | 2.6 | — | 4.6 | 2.6 | 14 | 7.3 | 14 | 10
10 (254) | — | 9.8 | 3.4 | — | 6.1 | 3.4 | 18 | 8.8 | 18 | 14
12 (305) | — | 12 | 4 | — | 7.6 | 4 | 22 | 11 | 22 | 17
14 (356) | — | — | 4.9 | — | — | 4.9 | 26 | 14 | 26 | 20
16 (406) | — | — | 5.5 | — | — | 5.5 | 29 | 15 | 29 | 23
18 (457) | — | — | 6.1 | — | — | 6.1 | 35 | 18 | 35 | 27
20 (508) | — | — | — | — | — | — | 43 | 21 | 43 | 33
24 (610) | — | — | — | — | — | — | 50 | 25 | 50 | 40
Note: Enter table for losses at smallest diameter d.

## Table 24
I-P
Table 24 Valve Losses in Equivalent Feet of Pipe
Nominal
Pipe or
Tube Size, |  | 60° | 45° |  |  | Swing | Lift
in | Globe | Wye | Wye | Angle | Gate | Check | Check
3/8 | 17 | 8 | 6 | 6 | 0.6 | 5 | Globe
1/2 | 18 | 9 | 7 | 7 | 0.7 | 6 | and
3/4 | 22 | 11 | 9 | 9 | 0.9 | 8 | vertical
1 | 29 | 15 | 12 | 12 | 1 | 10 | lift
1 1/4 | 38 | 20 | 15 | 15 | 1.5 | 14 | same as
1 1/2 | 43 | 24 | 18 | 18 | 1.8 | 16 | globe
2 | 55 | 30 | 24 | 24 | 2.3 | 20 | valved
2 1/2 | 69 | 35 | 29 | 29 | 2.8 | 25
3 | 84 | 43 | 35 | 35 | 3.2 | 30
3 1/2 | 100 | 50 | 41 | 41 | 4 | 35
4 | 120 | 58 | 47 | 47 | 4.5 | 40
5 | 140 | 71 | 58 | 58 | 6 | 50
6 | 170 | 88 | 70 | 70 | 7 | 60
8 | 220 | 115 | 85 | 85 | 9 | 80 | Angle
10 | 280 | 145 | 105 | 105 | 12 | 100 | lift
12 | 320 | 165 | 130 | 130 | 13 | 120 | same as
14 | 360 | 185 | 155 | 155 | 15 | 135 | angle
16 | 410 | 210 | 180 | 180 | 17 | 150 | valve
18 | 460 | 240 | 200 | 200 | 19 | 165
20 | 520 | 275 | 235 | 235 | 22 | 200
24 | 610 | 320 | 265 | 265 | 25 | 240
Note: Losses are for valves in fully open position and with screwed, welded, flanged or flared connections
aThese losses do not apply to valves with needlepoint seats.
bRegular and short pattern plug cock valves, when fully open, have same loss as gate valve. For valve losses of short pattern plug cocks above 6 in., check with manufacturer.
cLosses also apply to in-line, ball check valve.
dFor Y pattern globe lift check valve with seat approximately equal to nominal pipe diameter, use values of 60° wye valve for loss.
SI
Table 24 Valve Losses in Equivalent Meters of Pipe
Nominal
Pipe or
Tube Size, |  | 60° | 45° |  |  | Swing | Lift
in (mm) | Globe | Wye | Wye | Angle | Gate | Check | Check
3/8 (10) | 5.2 | 2.4 | 1.8 | 1.8 | 0.2 | 1.5 | Globe
1/2 (13) | 5.5 | 2.7 | 2.1 | 2.1 | 0.2 | 1.8 | and
3/4 (19) | 6.7 | 3.4 | 2.1 | 2.1 | 0.3 | 2.2 | vertical
1 (25) | 8.8 | 4.6 | 3.7 | 3.7 | 0.3 | 3 | lift
1 1/4 (32) | 12 | 6.1 | 4.6 | 4.6 | 0.5 | 4.3 | same as
1 1/2 (38) | 13 | 7.3 | 5.5 | 5.5 | 0.5 | 4.9 | globe
2 (51) | 17 | 9.1 | 7.3 | 7.3 | 0.73 | 6.1 | valved
2 1/2 (64) | 21 | 11 | 8.8 | 8.8 | 0.9 | 7.6
3 (76) | 26 | 13 | 11 | 11 | 1 | 9.1
3 1/2 (89) | 30 | 15 | 13 | 13 | 1.2 | 10
4 (102) | 37 | 18 | 14 | 14 | 1.4 | 12
5 (127) | 43 | 22 | 18 | 18 | 1.8 | 15
6 (152) | 52 | 27 | 21 | 21 | 2.1 | 18
8 (203) | 62 | 35 | 26 | 26 | 2.7 | 24 | Angle
10 (254) | 85 | 44 | 32 | 32 | 3.7 | 30 | lift
12 (305) | 98 | 50 | 40 | 40 | 4 | 37 | same as
14 (356) | 110 | 56 | 47 | 47 | 4.6 | 41 | angle
16 (406) | 125 | 64 | 55 | 55 | 5.2 | 46 | valve
18 (457) | 140 | 73 | 61 | 61 | 5.8 | 50
20 (508) | 160 | 84 | 72 | 72 | 6.7 | 61
24 (610) | 186 | 98 | 81 | 81 | 7.6 | 73
Note: Losses are for valves in fully open position and with screwed, welded, flanged or flared connections
aThese losses do not apply to valves with needlepoint seats.
bRegular and short pattern plug cock valves, when fully open, have same loss as gate valve. For valve losses of short pattern plug cocks above 6 in., check with manufacturer.
cLosses also apply to in-line, ball check valve.
dFor Y pattern globe lift check valve with seat approximately equal to nominal pipe diameter, use values of 60° wye valve for loss.

## Example 3
I-P
Example 3. Determine the maximum size suction and discharge riser that will transport
oil at minimum loading, using R-454B with a 40 ton compressor having capacity steps of
of 25, 50, 75 and 100 percent. Minimum system loading is 10 tons at 40°F evaporator
and 100°F condenser temperature with 25°F superheated refrigerant entering the compressor.
Solution: From Table 25, the minimum rating for the 2-1/8" OD suction riser at 40°F evaporator,
25°F superheat and 105°F liquid to transport oil is approximately 8.56 tons. Use Note 1,
to determine capacity at 100°F condensing and zero subcooling:
Actual minimum 2-1/8" OD line capacity | = | 8.56 x 1.03 = | 8.8 tons
Simple inspection shows the 2-5/8" OD suction riser is too large.
From Table 26, the minimum capacity for the 1-5/8" OD discharge riser at 40°F evaporator,
25°F superheat and 100°F condensing to transport oil is 6.21 tons. The 2-1/8" OD riser
having a 12.4 ton minumum capacity is too large.
SI
Example 3. Determine the maximum size suction and discharge riser that will transport
oil at minimum loading, using R-454B with a 140 kW compressor having capacity steps of
of 25, 50, 75 and 100 percent. Minimum system loading is 35 kW at 5°C evaporator
and 35°C condenser temperature with 14 K superheated refrigerant entering the compressor.
Solution: From Table 25, the minimum rating for the 54 mm OD suction riser at 5°C evaporator,
14 K superheat and 40°C liquid to transport oil is approximately 30.5 kW. Use Note 1,
to determine capacity at 35°C condensing and zero subcooling:
Actual minimum 54 mm OD line capacity | = | 30.5 x 1.05 = | 32.0 kW
Simple inspection shows the 67 mm OD suction riser is too large.
From Table 26, the minimum capacity for the 41 mm OD discharge riser at 5°C evaporator,
14 K superheat and 35°C condensing to transport oil is approximately 21.8 kW. The 54 mm OD
riser having approximately a 43.7 kW minumum capacity is too large.

## Table 25
I-P
Table 25 Minimum Refrigeration Capacity in Tons for Oil Entrainment up Suction Risers (Type L Copper Tubing)
Pipe OD, in
|  |  | 1/2 | 5/8 | 3/4 | 7/8 | 1 1/8 | 1 3/8 | 1 5/8 | 2 1/8 | 2 5/8 | 3 1/8 | 3 5/8 | 4 1/8
Pipe ID, in
|  | Suction | 0.436 | 0.545 | 0.666 | 0.785 | 1.025 | 1.265 | 1.505 | 1.985 | 2.465 | 2.945 | 3.425 | 3.905
Refrig- | Evap | Gas | Area, in2
erant | Temp, °F | Temp, °F | 0.1493 | 0.23328 | 0.34837 | 0.48398 | 0.82516 | 1.2568 | 1.7789 | 3.0946 | 4.7723 | 6.8118 | 9.2132 | 11.9766
448A/ | -40 | -30 | 0.052053 | 0.090933 | 0.15011 | 0.22641 | 0.4411 | 0.74637 | 1.1523 | 2.3021 | 3.9561 | 6.1723 | 9.0029 | 12.4963
449A |  | -10 | 0.050448 | 0.08813 | 0.14548 | 0.21944 | 0.42751 | 0.72337 | 1.1168 | 2.2312 | 3.8342 | 5.982 | 8.7254 | 12.1111
|  | 10 | 0.048978 | 0.085561 | 0.14124 | 0.21304 | 0.41504 | 0.70228 | 1.0842 | 2.1661 | 3.7224 | 5.8076 | 8.471 | 11.7581
| -20 | -10 | 0.069551 | 0.1215 | 0.20057 | 0.30253 | 0.58939 | 0.99728 | 1.5397 | 3.076 | 5.2861 | 8.2471 | 12.0293 | 16.6971
|  | 10 | 0.067389 | 0.11772 | 0.19434 | 0.29312 | 0.57106 | 0.96627 | 1.4918 | 2.9804 | 5.1217 | 7.9907 | 11.6553 | 16.178
|  | 30 | 0.065418 | 0.11428 | 0.18865 | 0.28455 | 0.55436 | 0.93801 | 1.4482 | 2.8932 | 4.9719 | 7.757 | 11.3144 | 15.7048
| 0 | 10 | 0.090341 | 0.15782 | 0.26053 | 0.39296 | 0.76556 | 1.2954 | 1.9999 | 3.9955 | 6.8661 | 10.7123 | 15.625 | 21.6881
|  | 30 | 0.087476 | 0.15281 | 0.25227 | 0.38049 | 0.74128 | 1.2543 | 1.9365 | 3.8688 | 6.6484 | 10.3726 | 15.1296 | 21.0004
|  | 50 | 0.084885 | 0.14829 | 0.2448 | 0.36923 | 0.71933 | 1.2171 | 1.8791 | 3.7542 | 6.4515 | 10.0654 | 14.6814 | 20.3784
| 20 | 30 | 0.11453 | 0.20007 | 0.33027 | 0.49815 | 0.97051 | 1.6422 | 2.5353 | 5.0651 | 8.7043 | 13.5801 | 19.808 | 27.4943
|  | 50 | 0.11078 | 0.19352 | 0.31947 | 0.48186 | 0.93876 | 1.5884 | 2.4524 | 4.8994 | 8.4195 | 13.1358 | 19.16 | 26.5948
|  | 70 | 0.10742 | 0.18766 | 0.30979 | 0.46726 | 0.91032 | 1.5403 | 2.3781 | 4.751 | 8.1644 | 12.7379 | 18.5795 | 25.7891
| 40 | 50 | 0.14214 | 0.24831 | 0.40992 | 0.61828 | 1.2045 | 2.0382 | 3.1467 | 6.2866 | 10.8032 | 16.8548 | 24.5846 | 34.1243
|  | 70 | 0.13728 | 0.23983 | 0.39591 | 0.59715 | 1.1634 | 1.9685 | 3.0391 | 6.0717 | 10.4339 | 16.2787 | 23.7442 | 32.9578
|  | 90 | 0.13299 | 0.23232 | 0.38351 | 0.57844 | 1.1269 | 1.9068 | 2.9439 | 5.8815 | 10.1072 | 15.7689 | 23.0006 | 31.9257
454B | -40 | -30 | 0.083338 | 0.14559 | 0.24033 | 0.36249 | 0.70621 | 1.195 | 1.8449 | 3.6858 | 6.3339 | 9.8819 | 14.4138 | 20.0069
|  | -10 | 0.080655 | 0.1409 | 0.23259 | 0.35082 | 0.68348 | 1.1565 | 1.7855 | 3.5671 | 6.13 | 9.5637 | 13.9497 | 19.3628
|  | 10 | 0.078224 | 0.13665 | 0.22559 | 0.34025 | 0.66288 | 1.1216 | 1.7317 | 3.4596 | 5.9452 | 9.2755 | 13.5294 | 18.7793
| -20 | -10 | 0.10713 | 0.18714 | 0.30894 | 0.46597 | 0.9078 | 1.5361 | 2.3715 | 4.7379 | 8.1419 | 12.7027 | 18.5282 | 25.7178
|  | 10 | 0.10362 | 0.18101 | 0.29882 | 0.45071 | 0.87808 | 1.4858 | 2.2938 | 4.5827 | 7.8753 | 12.2867 | 17.9215 | 24.8757
|  | 30 | 0.10046 | 0.1755 | 0.28972 | 0.43699 | 0.85135 | 1.4405 | 2.224 | 4.4432 | 7.6355 | 11.9127 | 17.376 | 24.1185
| 0 | 10 | 0.13441 | 0.23481 | 0.38762 | 0.58464 | 1.139 | 1.9273 | 2.9755 | 5.9445 | 10.2155 | 15.9379 | 23.2471 | 32.2679
|  | 30 | 0.12988 | 0.2269 | 0.37456 | 0.56495 | 1.1006 | 1.8624 | 2.8753 | 5.7443 | 9.8715 | 15.4011 | 22.4642 | 31.1811
|  | 50 | 0.12585 | 0.21985 | 0.36293 | 0.54741 | 1.0665 | 1.8045 | 2.786 | 5.566 | 9.565 | 14.9229 | 21.7667 | 30.213
| 20 | 30 | 0.16514 | 0.28848 | 0.47622 | 0.71829 | 1.3994 | 2.3678 | 3.6557 | 7.3034 | 12.5507 | 19.5811 | 28.5612 | 39.644
|  | 50 | 0.15935 | 0.27837 | 0.45953 | 0.6931 | 1.3503 | 2.2848 | 3.5275 | 7.0473 | 12.1106 | 18.8946 | 27.5597 | 38.2539
|  | 70 | 0.15425 | 0.26946 | 0.44482 | 0.67093 | 1.3071 | 2.2117 | 3.4146 | 6.8218 | 11.7231 | 18.29 | 26.6779 | 37.03
| 40 | 50 | 0.19915 | 0.3479 | 0.57431 | 0.86624 | 1.6876 | 2.8556 | 4.4086 | 8.8078 | 15.1358 | 23.6144 | 34.4442 | 47.8098 | 8.5634
|  | 70 | 0.19178 | 0.33503 | 0.55307 | 0.83419 | 1.6252 | 2.7499 | 4.2455 | 8.4819 | 14.5759 | 22.7408 | 33.1698 | 46.041
|  | 90 | 0.18539 | 0.32386 | 0.53463 | 0.80639 | 1.571 | 2.6583 | 4.104 | 8.1992 | 14.09 | 21.9828 | 32.0642 | 44.5064
Notes:
1. Minimum refrigeration capacity is determined at 105°F liquid temperature and using ISO 32 POE oil. For other liquid temperatures, use correction factors listed in the table below. Correction factors based on a 0°F evaporator temperature, and are suitable in the range of -40°F to 40°F.
Liquid Temperature, °F
Refrigerant |  | 80 | 90 | 100 | 110 | 120 | 130 | 140
448A/449A |  | 1.1741 | 1.1059 | 1.0358 | 0.96362 | 0.88887 | 0.81093 | 0.72876
454B |  | 1.1418 | 1.0864 | 1.0293 | 0.97008 | 0.90816 | 0.84271 | 0.77239
SI
Table 25 Minimum Refrigeration Capacity in Kilowatts for Oil Entrainment up Suction Risers (Type L Copper Tubing)
Pipe OD, in (mm)
|  |  | 1/2 (13) | 5/8 (16) | 3/4 (19) | 7/8 (22) | 1 1/8 (29) | 1 3/8 (35) | 1 5/8 (41) | 2 1/8 (54) | 2 5/8 (67) | 3 1/8 (79) | 3 5/8 (92) | 4 1/8 (105)
Pipe ID, mm
|  | Suction | 11.0744 | 13.843 | 16.9164 | 19.939 | 26.035 | 32.131 | 38.227 | 50.419 | 62.611 | 74.803 | 86.995 | 99.187
Refrig- | Evap | Gas | Area, cm2
erant | Temp, °C | Temp, °C | 0.96323 | 1.505 | 2.2475 | 3.1225 | 5.3236 | 8.1085 | 11.4771 | 19.9654 | 30.7887 | 43.9469 | 59.44 | 77.268
448A/ | -40 | -35 | 0.1847 | 0.32266 | 0.53265 | 0.80339 | 1.5652 | 2.6484 | 4.0888 | 8.1688 | 14.0377 | 21.9012 | 31.9452 | 44.3412
449A |  | -25 | 0.17954 | 0.31364 | 0.51776 | 0.78093 | 1.5214 | 2.5743 | 3.9745 | 7.9404 | 13.6453 | 21.2889 | 31.0522 | 43.1016
|  | -15 | 0.17477 | 0.30531 | 0.50401 | 0.7602 | 1.481 | 2.506 | 3.869 | 7.7296 | 13.283 | 20.7237 | 30.2278 | 41.9573
| -30 | -25 | 0.23998 | 0.41922 | 0.69206 | 1.0438 | 2.0336 | 3.441 | 5.3125 | 10.6135 | 18.2389 | 28.4557 | 41.5056 | 57.6113
|  | -15 | 0.23322 | 0.40741 | 0.67255 | 1.0144 | 1.9763 | 3.344 | 5.1628 | 10.3144 | 17.7249 | 27.6538 | 40.3361 | 55.988
|  | -5 | 0.227 | 0.39656 | 0.65464 | 0.9874 | 1.9237 | 3.2549 | 5.0253 | 10.0397 | 17.2528 | 26.9173 | 39.2617 | 54.4967
| -20 | -15 | 0.30465 | 0.5322 | 0.87856 | 1.3251 | 2.5816 | 4.3683 | 6.7441 | 13.4737 | 23.154 | 36.1242 | 52.6909 | 73.137
|  | -5 | 0.29592 | 0.51695 | 0.85338 | 1.2872 | 2.5076 | 4.2431 | 6.5509 | 13.0876 | 22.4905 | 35.089 | 51.181 | 71.0411
|  | 5 | 0.28795 | 0.50303 | 0.8304 | 1.2525 | 2.4401 | 4.1288 | 6.3744 | 12.7351 | 21.8848 | 34.1439 | 49.8025 | 69.1277
| -5 | 0 | 0.41988 | 0.7335 | 1.2109 | 1.8264 | 3.5581 | 6.0206 | 9.295 | 18.57 | 31.9119 | 49.7879 | 72.6209 | 100.8005
|  | 10 | 0.40732 | 0.71155 | 1.1746 | 1.7717 | 3.4517 | 5.8404 | 9.0169 | 18.0143 | 30.957 | 48.2981 | 70.448 | 97.7844
|  | 20 | 0.39599 | 0.69176 | 1.142 | 1.7224 | 3.3556 | 5.678 | 8.7661 | 17.5133 | 30.096 | 46.9547 | 68.4884 | 95.0645
| 5 | 10 | 0.50901 | 0.8892 | 1.4679 | 2.214 | 4.3134 | 7.2985 | 11.268 | 22.5116 | 38.6855 | 60.3558 | 88.0354 | 122.1964
|  | 20 | 0.49312 | 0.86145 | 1.4221 | 2.1449 | 4.1788 | 7.0707 | 10.9164 | 21.8092 | 37.4784 | 58.4725 | 85.2884 | 118.3835
|  | 30 | 0.47895 | 0.83669 | 1.3812 | 2.0833 | 4.0587 | 6.8676 | 10.6027 | 21.1825 | 36.4014 | 56.7922 | 82.8375 | 114.9816
454B | -40 | -35 | 0.29523 | 0.51575 | 0.85139 | 1.2842 | 2.5018 | 4.2332 | 6.5356 | 13.0571 | 22.4381 | 35.0072 | 51.0618 | 70.8757
|  | -25 | 0.2866 | 0.50067 | 0.8265 | 1.2466 | 2.4287 | 4.1095 | 6.3445 | 12.6753 | 21.7822 | 33.9838 | 49.569 | 68.8036
|  | -15 | 0.27872 | 0.4869 | 0.80378 | 1.2123 | 2.3619 | 3.9965 | 6.1701 | 12.3269 | 21.1833 | 33.0495 | 48.2063 | 66.9121
| -30 | -25 | 0.37047 | 0.64718 | 1.0684 | 1.6114 | 3.1394 | 5.312 | 8.2011 | 16.3845 | 28.1562 | 43.9284 | 64.0743 | 88.9375
|  | -15 | 0.35947 | 0.62796 | 1.0366 | 1.5636 | 3.0462 | 5.1543 | 7.9576 | 15.898 | 27.3202 | 42.6241 | 62.1718 | 86.2968
|  | -5 | 0.34949 | 0.61053 | 1.0079 | 1.5202 | 2.9616 | 5.0112 | 7.7367 | 15.4567 | 26.5619 | 41.4409 | 60.446 | 83.9013
| -20 | -15 | 0.45573 | 0.79613 | 1.3143 | 1.9823 | 3.8619 | 6.5346 | 10.0887 | 20.1556 | 34.6366 | 54.0389 | 78.8215 | 109.4072
|  | -5 | 0.44186 | 0.7719 | 1.2743 | 1.922 | 3.7444 | 6.3357 | 9.7816 | 19.5421 | 33.5825 | 52.3943 | 76.4227 | 106.0775
|  | 5 | 0.42938 | 0.75009 | 1.2383 | 1.8677 | 3.6386 | 6.1567 | 9.5053 | 18.99 | 32.6336 | 50.9139 | 74.2634 | 103.0803
| -5 | 0 | 0.60217 | 1.0519 | 1.7366 | 2.6192 | 5.1028 | 8.6343 | 13.3304 | 26.632 | 45.7662 | 71.4028 | 104.1487 | 144.5622
|  | 10 | 0.58279 | 1.0181 | 1.6807 | 2.535 | 4.9386 | 8.3565 | 12.9015 | 25.7751 | 44.2936 | 69.1053 | 100.7975 | 139.9107
|  | 20 | 0.56561 | 0.98808 | 1.6311 | 2.4602 | 4.793 | 8.1101 | 12.5211 | 25.0151 | 42.9875 | 67.0677 | 97.8254 | 135.7853
| 5 | 10 | 0.71161 | 1.2431 | 2.0522 | 3.0953 | 6.0303 | 10.2036 | 15.7532 | 31.4723 | 54.084 | 84.3801 | 123.0774 | 170.836
|  | 20 | 0.68751 | 1.201 | 1.9827 | 2.9905 | 5.8261 | 9.8581 | 15.2197 | 30.4065 | 52.2526 | 81.5228 | 118.9097 | 165.0511 | 1.1 | 0.11
|  | 30 | 0.66642 | 1.1642 | 1.9218 | 2.8987 | 5.6473 | 9.5556 | 14.7527 | 29.4735 | 50.6493 | 79.0213 | 115.261 | 159.9866
Notes:
1. Minimum refrigeration capacity is determined at 40°C liquid temperature and using ISO 32 POE oil. For other liquid temperatures, use correction factors listed in the table below. Correction factors based on a -18°C evaporator temperature, and are suitable in the range of -40°C to 5°C.
Liquid Temperature, °C
Refrigerant |  | 25 | 30 | 35 | 45 | 50 | 55 | 60
448A/449A |  | 1.1859 | 1.1254 | 1.0635 | 0.93469 | 0.86719 | 0.79699 | 0.72329
454B |  | 1.1513 | 1.1023 | 1.0519 | 0.9462 | 0.89007 | 0.83093 | 0.76773

## Table 26
I-P
Table 26 Minimum Refrigeration Capacity in Tons for Oil Entrainment up Hot-Gas Risers (Type L Copper Tubing)
Pipe OD, in
|  |  | 1/2 | 5/8 | 3/4 | 7/8 | 1 1/8 | 1 3/8 | 1 5/8 | 2 1/8 | 2 5/8 | 3 1/8 | 3 5/8 | 4 1/8
Pipe ID, in
|  |  | 0.436 | 0.545 | 0.666 | 0.785 | 1.025 | 1.265 | 1.505 | 1.985 | 2.465 | 2.945 | 3.425 | 3.905
Refrig- | Evap | Cond | Area, in2
erant | Temp, °F | Temp, °F | 0.1493 | 0.23328 | 0.34837 | 0.48398 | 0.82516 | 1.2568 | 1.7789 | 3.0946 | 4.7723 | 6.8118 | 9.2132 | 11.9766
448A/ | -40 | 80 | 0.17088 | 0.29851 | 0.49278 | 0.74327 | 1.448 | 2.4502 | 3.7828 | 7.5574 | 12.9872 | 20.2621 | 29.5545 | 41.0227
449A |  | 100 | 0.16689 | 0.29155 | 0.4813 | 0.72594 | 1.4143 | 2.3931 | 3.6946 | 7.3812 | 12.6844 | 19.7897 | 28.8654 | 40.0662
|  | 120 | 0.15629 | 0.27302 | 0.4507 | 0.67979 | 1.3244 | 2.2409 | 3.4597 | 6.912 | 11.878 | 18.5317 | 27.0304 | 37.5193
| -20 | 80 | 0.18419 | 0.32177 | 0.53117 | 0.80117 | 1.5609 | 2.6411 | 4.0775 | 8.1462 | 13.9989 | 21.8406 | 31.8569 | 44.2185
|  | 100 | 0.18108 | 0.31634 | 0.52221 | 0.78765 | 1.5345 | 2.5965 | 4.0087 | 8.0087 | 13.7626 | 21.472 | 31.3191 | 43.4721
|  | 120 | 0.17118 | 0.29905 | 0.49367 | 0.7446 | 1.4506 | 2.4546 | 3.7896 | 7.571 | 13.0104 | 20.2984 | 29.6074 | 41.0962
| 0 | 80 | 0.19721 | 0.3445 | 0.56871 | 0.85778 | 1.6711 | 2.8277 | 4.3656 | 8.7218 | 14.9881 | 23.3839 | 34.1079 | 47.3431
|  | 100 | 0.19499 | 0.34063 | 0.56231 | 0.84814 | 1.6524 | 2.7959 | 4.3165 | 8.6237 | 14.8196 | 23.121 | 33.7245 | 46.8108
|  | 120 | 0.18584 | 0.32465 | 0.53593 | 0.80834 | 1.5748 | 2.6647 | 4.114 | 8.219 | 14.1242 | 22.036 | 32.1419 | 44.6142
| 20 | 80 | 0.20981 | 0.36653 | 0.60506 | 0.91262 | 1.778 | 3.0084 | 4.6447 | 9.2793 | 15.9462 | 24.8788 | 36.2883 | 50.3695
|  | 100 | 0.20848 | 0.3642 | 0.60123 | 0.90683 | 1.7667 | 2.9894 | 4.6152 | 9.2205 | 15.8451 | 24.721 | 36.0582 | 50.0501
|  | 120 | 0.20009 | 0.34954 | 0.57702 | 0.87032 | 1.6956 | 2.869 | 4.4294 | 8.8492 | 15.207 | 23.7255 | 34.6062 | 48.0347
| 40 | 80 | 0.22188 | 0.38761 | 0.63987 | 0.96512 | 1.8803 | 3.1815 | 4.9119 | 9.8132 | 16.8636 | 26.31 | 38.376 | 53.2673
|  | 100 | 0.22141 | 0.38679 | 0.63851 | 0.96306 | 1.8762 | 3.1747 | 4.9014 | 9.7922 | 16.8276 | 26.2538 | 38.294 | 53.1535
|  | 120 | 0.21375 | 0.3734 | 0.61642 | 0.92974 | 1.8113 | 3.0649 | 4.7318 | 9.4534 | 16.2454 | 25.3455 | 36.9692 | 51.3146
454B | -40 | 80 | 0.2192 | 0.38293 | 0.63213 | 0.95345 | 1.8575 | 3.143 | 4.8525 | 9.6945 | 16.6596 | 25.9918 | 37.9118 | 52.623
|  | 100 | 0.21791 | 0.38067 | 0.62841 | 0.94783 | 1.8466 | 3.1245 | 4.8239 | 9.6374 | 16.5615 | 25.8387 | 37.6884 | 52.313
|  | 120 | 0.20983 | 0.36656 | 0.60511 | 0.91269 | 1.7781 | 3.0087 | 4.6451 | 9.2801 | 15.9475 | 24.8808 | 36.2913 | 50.3737
| -20 | 80 | 0.23511 | 0.41071 | 0.678 | 1.0226 | 1.9923 | 3.3711 | 5.2046 | 10.3979 | 17.8685 | 27.8778 | 40.6628 | 56.4415
|  | 100 | 0.23434 | 0.40937 | 0.67579 | 1.0193 | 1.9858 | 3.3601 | 5.1876 | 10.3639 | 17.8101 | 27.7867 | 40.5298 | 56.2569
|  | 120 | 0.22653 | 0.39573 | 0.65327 | 0.98532 | 1.9196 | 3.2481 | 5.0147 | 10.0186 | 17.2166 | 26.8607 | 39.1792 | 54.3823
| 0 | 80 | 0.25064 | 0.43785 | 0.72281 | 1.0902 | 2.124 | 3.5939 | 5.5485 | 11.085 | 19.0493 | 29.72 | 43.3498 | 60.1711
|  | 100 | 0.25036 | 0.43736 | 0.72199 | 1.089 | 2.1216 | 3.5898 | 5.5423 | 11.0726 | 19.0279 | 29.6866 | 43.3011 | 60.1036
|  | 120 | 0.24279 | 0.42414 | 0.70017 | 1.0561 | 2.0575 | 3.4813 | 5.3748 | 10.738 | 18.4528 | 28.7895 | 41.9925 | 58.2872
| 20 | 80 | 0.26568 | 0.46413 | 0.76618 | 1.1556 | 2.2514 | 3.8095 | 5.8815 | 11.7502 | 20.1923 | 31.5034 | 45.9511 | 63.7818
|  | 100 | 0.26583 | 0.46439 | 0.76661 | 1.1563 | 2.2527 | 3.8117 | 5.8848 | 11.7569 | 20.2038 | 31.5212 | 45.9771 | 63.8179
|  | 120 | 0.25846 | 0.4515 | 0.74534 | 1.1242 | 2.1902 | 3.7059 | 5.7215 | 11.4307 | 19.6433 | 30.6468 | 44.7016 | 62.0474
| 40 | 80 | 0.28005 | 0.48924 | 0.80763 | 1.2182 | 2.3732 | 4.0156 | 6.1997 | 12.3859 | 21.2848 | 33.2078 | 48.4371 | 67.2325
|  | 100 | 0.28056 | 0.49011 | 0.80908 | 1.2203 | 2.3775 | 4.0228 | 6.2108 | 12.4081 | 21.3229 | 33.2673 | 48.5239 | 67.353
|  | 120 | 0.27329 | 0.47742 | 0.78812 | 1.1887 | 2.3159 | 3.9186 | 6.0499 | 12.0868 | 20.7707 | 32.4058 | 47.2673 | 65.6088
Notes:
1. Minimum refrigeration capacity is determined at 0°F subcooling and using ISO 32 POE oil. Discharge refrigerant state determined with compression at 70 percent isentropic efficiency and 25°F superheated refrigerant entering the compressor.
SI
Table 26 Minimum Refrigeration Capacity in Kilowatts for Oil Entrainment up Hot-Gas Risers (Type L Copper Tubing)
Pipe OD, in (mm)
|  |  | 1/2 (13) | 5/8 (16) | 3/4 (19) | 7/8 (22) | 1 1/8 (29) | 1 3/8 (35) | 1 5/8 (41) | 2 1/8 (54) | 2 5/8 (67) | 3 1/8 (79) | 3 5/8 (92) | 4 1/8 (105)
Pipe ID, mm
|  |  | 11.0744 | 13.843 | 16.9164 | 19.939 | 26.035 | 32.131 | 38.227 | 50.419 | 62.611 | 74.803 | 86.995 | 99.187
Refrig- | Evap | Cond | Area, cm2
erant | Temp, °C | Temp, °C | 0.96323 | 1.505 | 2.2475 | 3.1225 | 5.3236 | 8.1085 | 11.4771 | 19.9654 | 30.7887 | 43.9469 | 59.44 | 77.268
448A/ | -40 | 30 | 0.59832 | 1.0452 | 1.7255 | 2.6025 | 5.0702 | 8.5792 | 13.2453 | 26.4619 | 45.4738 | 70.9468 | 103.4834 | 143.6389
449A |  | 40 | 0.58094 | 1.0149 | 1.6753 | 2.5269 | 4.9229 | 8.3299 | 12.8604 | 25.6929 | 44.1525 | 68.8852 | 100.4764 | 139.465
|  | 50 | 0.54386 | 0.95008 | 1.5684 | 2.3656 | 4.6087 | 7.7982 | 12.0395 | 24.053 | 41.3343 | 64.4884 | 94.0632 | 130.5632
| -30 | 30 | 0.64132 | 1.1203 | 1.8495 | 2.7896 | 5.4346 | 9.1957 | 14.1972 | 28.3636 | 48.742 | 76.0456 | 110.9206 | 153.9619
|  | 40 | 0.62633 | 1.0941 | 1.8062 | 2.7243 | 5.3076 | 8.9807 | 13.8652 | 27.7004 | 47.6022 | 74.2673 | 108.3268 | 150.3617
|  | 50 | 0.59118 | 1.0328 | 1.7049 | 2.5715 | 5.0097 | 8.4768 | 13.0872 | 26.146 | 44.9311 | 70.1 | 102.2483 | 141.9245
| -20 | 30 | 0.68352 | 1.1941 | 1.9712 | 2.9731 | 5.7922 | 9.8008 | 15.1313 | 30.2298 | 51.9489 | 81.049 | 118.2186 | 164.0918
|  | 40 | 0.67097 | 1.1721 | 1.935 | 2.9185 | 5.6859 | 9.6209 | 14.8535 | 29.6749 | 50.9953 | 79.5612 | 116.0484 | 161.0796
|  | 50 | 0.63786 | 1.1143 | 1.8395 | 2.7745 | 5.4053 | 9.1461 | 14.1206 | 28.2106 | 48.479 | 75.6353 | 110.3222 | 153.1313
| -5 | 30 | 0.74465 | 1.3008 | 2.1474 | 3.239 | 6.3102 | 10.6773 | 16.4845 | 32.9333 | 56.5947 | 88.2972 | 128.7908 | 178.7665
|  | 40 | 0.73577 | 1.2853 | 2.1218 | 3.2004 | 6.235 | 10.5499 | 16.2879 | 32.5405 | 55.9198 | 87.2442 | 127.255 | 176.6347
|  | 50 | 0.70577 | 1.2329 | 2.0353 | 3.0699 | 5.9808 | 10.1198 | 15.6238 | 31.2139 | 53.64 | 83.6873 | 122.0668 | 169.4333
| 5 | 30 | 0.78345 | 1.3686 | 2.2593 | 3.4078 | 6.639 | 11.2336 | 17.3435 | 34.6494 | 59.5438 | 92.8982 | 135.502 | 188.0818
|  | 40 | 0.77693 | 1.3572 | 2.2405 | 3.3794 | 6.5837 | 11.1401 | 17.199 | 34.3609 | 59.048 | 92.1248 | 134.3738 | 186.5159
|  | 50 | 0.74894 | 1.3084 | 2.1598 | 3.2577 | 6.3466 | 10.7389 | 16.5796 | 33.1234 | 56.9214 | 88.8069 | 129.5343 | 179.7985
454B | -40 | 30 | 0.77094 | 1.3468 | 2.2233 | 3.3533 | 6.533 | 11.0543 | 17.0665 | 34.0962 | 58.5931 | 91.415 | 133.3385 | 185.0788
|  | 40 | 0.76203 | 1.3312 | 2.1976 | 3.3146 | 6.4575 | 10.9265 | 16.8692 | 33.7019 | 57.9157 | 90.3581 | 131.7969 | 182.939
|  | 50 | 0.73279 | 1.2801 | 2.1132 | 3.1874 | 6.2097 | 10.5072 | 16.2219 | 32.4088 | 55.6934 | 86.891 | 126.7398 | 175.9196
| -30 | 30 | 0.82185 | 1.4357 | 2.3701 | 3.5748 | 6.9644 | 11.7842 | 18.1934 | 36.3475 | 62.462 | 97.4512 | 142.1429 | 197.2997
|  | 40 | 0.81427 | 1.4225 | 2.3482 | 3.5418 | 6.9002 | 11.6755 | 18.0257 | 36.0124 | 61.8861 | 96.5526 | 140.8322 | 195.4804
|  | 50 | 0.78567 | 1.3725 | 2.2657 | 3.4174 | 6.6578 | 11.2654 | 17.3925 | 34.7474 | 59.7123 | 93.1612 | 135.8855 | 188.6141
| -20 | 30 | 0.8717 | 1.5228 | 2.5138 | 3.7916 | 7.3868 | 12.499 | 19.297 | 38.5523 | 66.2507 | 103.3622 | 150.7648 | 209.2672
|  | 40 | 0.86537 | 1.5117 | 2.4956 | 3.7641 | 7.3333 | 12.4083 | 19.157 | 38.2726 | 65.7702 | 102.6125 | 149.6712 | 207.7493
|  | 50 | 0.83735 | 1.4628 | 2.4148 | 3.6422 | 7.0958 | 12.0066 | 18.5368 | 37.0334 | 63.6407 | 99.29 | 144.8251 | 201.0226
| -5 | 30 | 0.94376 | 1.6487 | 2.7217 | 4.1051 | 7.9975 | 13.5323 | 20.8924 | 41.7396 | 71.7281 | 111.9077 | 163.2294 | 226.5685
|  | 40 | 0.93907 | 1.6405 | 2.7081 | 4.0846 | 7.9577 | 13.465 | 20.7884 | 41.5318 | 71.3711 | 111.3507 | 162.4169 | 225.4407
|  | 50 | 0.91168 | 1.5926 | 2.6291 | 3.9655 | 7.7257 | 13.0723 | 20.1822 | 40.3207 | 69.2897 | 108.1035 | 157.6804 | 218.8663
| 5 | 30 | 0.98934 | 1.7283 | 2.8531 | 4.3033 | 8.3838 | 14.1859 | 21.9014 | 43.7555 | 75.1923 | 117.3125 | 171.1128 | 237.511
|  | 40 | 0.98547 | 1.7215 | 2.8419 | 4.2865 | 8.351 | 14.1304 | 21.8157 | 43.5842 | 74.898 | 116.8533 | 170.443 | 236.5813
|  | 50 | 0.95824 | 1.674 | 2.7634 | 4.1681 | 8.1203 | 13.74 | 21.213 | 42.38 | 72.8286 | 113.6248 | 165.7339 | 230.0448
Notes:
1. Minimum refrigeration capacity is determined at 0 K subcooling and using ISO 32 POE oil. Discharge refrigerant state determined with compression at 70 percent isentropic efficiency and 14 K superheated refrigerant entering the compressor.

## Page 1.18 Table
I-P
Saturation | Line Size
Temperature, °F | 2 in. or less | Above 2 in.
0 | 0.35 psi/100 ft | 0.20 psi/100 ft
-50 | 0.45 psi/100 ft | 0.25 psi/100 ft
SI
Saturation | Line Size
Temperature, °C | 50 mm or less | Above 50 mm
-18 | 80 Pa/m | 45 Pa/m
-46 | 100 Pa/m | 57 Pa/m

## Example 4
I-P
Example 4. Determine the maximum size defrost line which will maintain a minimum refrigerant
velocity of 2000 fpm using R-448A at a condensing temperature of 70°F given a minimum
refrigerant flow rate of 10,000 lb/h.
Solution: From Table 27, the rating for the 2-5/8" OD defrost line is 10,900 lb/hr at 2000 fpm. As
a result, the 2-1/8" OD line must be used.
SI
Example 4. Determine the maximum size defrost line which will maintain a minimum refrigerant
velocity of 10 m/s using R-448A at a condensing temperature of 21°C given a minimum
refrigerant flow rate of 4000 kg/h.
Solution: From Table 27, the rating for the 67 mm OD defrost line is 4850 kg/hr at 10 m/s. As
a result, the 54 mm OD line must be used.

## Table 27
I-P
Table 27 Refrigerant Flow Capacity for Defrost Lines
Line Size |  | Refrigerant Mass Flow, lb/h
Type L, |  | R-448A/449A |  |  | R-454C |  |  | R-455A |  |  | R-457A
Copper, |  | Velocity, fpm
OD, in |  | 1000 | 2000 | 3000 | 1000 | 2000 | 3000 | 1000 | 2000 | 3000 | 1000 | 2000 | 3000
3/8 |  | 86.8 | 174 | 260 | 78.3 | 157 | 235 | 80.3 | 161 | 241 | 68.5 | 137 | 205
1/2 |  | 171 | 341 | 512 | 154 | 308 | 462 | 158 | 316 | 473 | 135 | 269 | 404
5/8 |  | 266 | 533 | 799 | 241 | 481 | 722 | 247 | 493 | 740 | 210 | 421 | 631
3/4 |  | 398 | 796 | 1190 | 359 | 718 | 1080 | 368 | 736 | 1100 | 314 | 628 | 942
7/8 |  | 553 | 1110 | 1660 | 499 | 998 | 1500 | 512 | 1020 | 1530 | 436 | 873 | 1310
1 1/8 |  | 942 | 1880 | 2830 | 851 | 1700 | 2550 | 872 | 1740 | 2620 | 744 | 1490 | 2230
1 3/8 |  | 1440 | 2870 | 4310 | 1300 | 2590 | 3890 | 1330 | 2660 | 3990 | 1130 | 2270 | 3400
1 5/8 |  | 2030 | 4060 | 6100 | 1830 | 3670 | 5500 | 1880 | 3760 | 5640 | 1600 | 3210 | 4810
2 1/8 |  | 3530 | 7070 | 10600 | 3190 | 6380 | 9570 | 3270 | 6540 | 9810 | 2790 | 5580 | 8370
2 5/8 |  | 5450 | 10900 | 16400 | 4920 | 9840 | 14800 | 5040 | 10100 | 15100 | 4300 | 8610 | 12900
3 1/8 |  | 7780 | 15600 | 23300 | 7020 | 14000 | 21100 | 7200 | 14400 | 21600 | 6140 | 12300 | 18400
3 5/8 |  | 10500 | 21000 | 31600 | 9500 | 19000 | 28500 | 9740 | 19500 | 29200 | 8310 | 16600 | 24900
4 1/8 |  | 13700 | 27400 | 41000 | 12300 | 24700 | 37000 | 12700 | 25300 | 38000 | 10800 | 21600 | 32400
Steel
IPS | SCH
3/8 | 80 | 160 | 321 | 481 | 145 | 290 | 435 | 149 | 297 | 446 | 127 | 253 | 380
1/2 | 80 | 267 | 535 | 802 | 241 | 483 | 724 | 247 | 495 | 742 | 211 | 422 | 633
3/4 | 80 | 494 | 988 | 1480 | 446 | 892 | 1340 | 457 | 914 | 1370 | 390 | 780 | 1170
1 | 80 | 822 | 1640 | 2460 | 742 | 1480 | 2220 | 760 | 1520 | 2280 | 649 | 1300 | 1950
1 1/4 | 80 | 1470 | 2930 | 4400 | 1320 | 2650 | 3970 | 1360 | 2710 | 4070 | 1160 | 2310 | 3470
1 1/2 | 80 | 2020 | 4040 | 6050 | 1820 | 3640 | 5470 | 1870 | 3740 | 5600 | 1590 | 3190 | 4780
2 | 40 | 3830 | 7660 | 11500 | 3460 | 6920 | 10400 | 3550 | 7090 | 10600 | 3030 | 6050 | 9080
2 1/2 | 40 | 5470 | 10900 | 16400 | 4940 | 9870 | 14800 | 5060 | 10100 | 15200 | 4320 | 8630 | 13000
3 | 40 | 8440 | 16900 | 25300 | 7620 | 15200 | 22900 | 7810 | 15600 | 23400 | 6670 | 13300 | 20000
4 | 40 | 14500 | 29100 | 43600 | 13100 | 26300 | 39400 | 13500 | 26900 | 40400 | 11500 | 23000 | 34400
Note: Refrigerant flow data based on 70°F condensing temperature at saturation.
SI
Table 27 Refrigerant Flow Capacity for Defrost Lines
Line Size |  | Refrigerant Mass Flow, kg/h
Type L, |  | R-448A/449A |  |  | R-454C |  |  | R-455A |  |  | R-457A
Copper, |  | Velocity, m/s
OD, in (mm) |  | 5 | 10 | 15 | 5 | 10 | 15 | 5 | 10 | 15 | 5 | 10 | 15
3/8 (10) |  | 38.6 | 77.2 | 116 | 34.9 | 69.7 | 105 | 35.7 | 71.5 | 107 | 30.5 | 61 | 91.4
1/2 (13) |  | 75.9 | 152 | 228 | 68.5 | 137 | 205 | 70.2 | 140 | 211 | 59.9 | 120 | 180
5/8 (16) |  | 119 | 237 | 356 | 107 | 214 | 321 | 110 | 219 | 329 | 93.6 | 187 | 281
3/4 (19) |  | 177 | 354 | 531 | 160 | 320 | 479 | 164 | 328 | 492 | 140 | 280 | 419
7/8 (22) |  | 246 | 492 | 738 | 222 | 444 | 666 | 228 | 455 | 683 | 194 | 388 | 583
1 1/8 (29) |  | 419 | 839 | 1260 | 379 | 757 | 1140 | 388 | 776 | 1160 | 331 | 662 | 993
1 3/8 (35) |  | 639 | 1280 | 1920 | 577 | 1150 | 1730 | 591 | 1180 | 1770 | 504 | 1010 | 1510
1 5/8 (41) |  | 904 | 1810 | 2710 | 816 | 1630 | 2450 | 837 | 1670 | 2510 | 714 | 1430 | 2140
2 1/8 (54) |  | 1570 | 3150 | 4720 | 1420 | 2840 | 4260 | 1460 | 2910 | 4370 | 1240 | 2480 | 3730
2 5/8 (67) |  | 2430 | 4850 | 7280 | 2190 | 4380 | 6570 | 2240 | 4490 | 6730 | 1910 | 3830 | 5740
3 1/8 (79) |  | 3460 | 6920 | 10400 | 3130 | 6250 | 9380 | 3200 | 6410 | 9610 | 2730 | 5470 | 8200
3 5/8 (92) |  | 4680 | 9360 | 14000 | 4230 | 8450 | 12700 | 4330 | 8670 | 13000 | 3700 | 7390 | 11100
4 1/8 (105) |  | 6090 | 12200 | 18300 | 5490 | 11000 | 16500 | 5630 | 11300 | 16900 | 4810 | 9610 | 14400
Steel
IPS (mm) | SCH
3/8 (10) | 80 | 71.4 | 143 | 214 | 64.5 | 129 | 193 | 66.1 | 132 | 198 | 56.4 | 113 | 169
1/2 (13) | 80 | 119 | 238 | 357 | 107 | 215 | 322 | 110 | 220 | 330 | 93.9 | 188 | 282
3/4 (19) | 80 | 220 | 439 | 659 | 198 | 397 | 595 | 203 | 407 | 610 | 174 | 347 | 521
1 (25) | 80 | 366 | 731 | 1100 | 330 | 660 | 990 | 338 | 677 | 1020 | 289 | 577 | 866
1 1/4 (32) | 80 | 652 | 1300 | 1960 | 589 | 1180 | 1770 | 603 | 1210 | 1810 | 515 | 1030 | 1540
1 1/2 (38) | 80 | 898 | 1800 | 2690 | 811 | 1620 | 2430 | 831 | 1660 | 2490 | 709 | 1420 | 2130
2 (51) | 40 | 1710 | 3410 | 5120 | 1540 | 3080 | 4620 | 1580 | 3160 | 4740 | 1350 | 2690 | 4040
2 1/2 (64) | 40 | 2430 | 4870 | 7300 | 2200 | 4390 | 6590 | 2250 | 4500 | 6760 | 1920 | 3840 | 5760
3 (76) | 40 | 3760 | 7510 | 11300 | 3390 | 6780 | 10200 | 3480 | 6950 | 10400 | 2970 | 5930 | 8900
4 (102) | 40 | 6470 | 12900 | 19400 | 5840 | 11700 | 17500 | 5990 | 12000 | 18000 | 5110 | 10200 | 15300
Note: Refrigerant flow data based on 21°C condensing temperature at saturation.

## Ch 48 Table 1
I-P
Table 1 Low Temperature Characteristics of Several Refrigerants at Three Evaporating Temperatures
|  | Pressure, psia |  |  | Pressure Ratio (per stage) |  |  | Volumetric Flow of
[5 empty] | with Two-Stage System |  |  | Refrigerant, CFM per ton
Refrig- | Freezing | Evaporating Temperature, °F
erant | Point1 | -60 | -95 | -130 | -60 | -95 | -130 | -60 | -95 | -130
R-404A | < -157°F | 11.1 | 3.65 | 0.89 | 4.6 | 8.02 | 16.2 | 11.1 | 30.2 | 108
R-410A | < -202°F | 14.9 | 4.96 | 1.25 | 4.57 | 7.92 | 15.8 | 7.91 | 21.2 | 73.8
R-448A | < -205°F | 8.23 | 2.48 | 0.54 | 5.42 | 9.86 | 21.1 | 13.6 | 40.3 | 161
R-449A | < -206°F | 8.27 | 2.51 | 0.55 | 5.36 | 9.74 | 20.7 | 13.6 | 39.9 | 158
R-454B | < -221°F | 13.5 | 4.52 | 1.14 | 4.66 | 8.08 | 16.1 | 8.54 | 23 | 80
R-717 | -108°F | 5.54 | 1.52 | 0.24 | 5.95 | 11.4 | 28.5 | 16.5 | 54.1 | 301
1Freezing point is determined at standard atmospheric pressure.
SI
Table 1 Low Temperature Characteristics of Several Refrigerants at Three Evaporating Temperatures
|  | Pressure, kPa |  |  | Pressure Ratio (per stage) |  |  | Volumetric Flow of
[5 empty] | with Two-Stage System |  |  | Refrigerant, L/s per kW
Refrig- | Freezing | Evaporating Temperature, °C
erant | Point1 | -50 | -70 | -90 | -50 | -70 | -90 | -50 | -70 | -90
R-404A | < -105°C | 81 | 26.1 | 6.16 | 4.47 | 7.88 | 16.2 | 1.42 | 3.93 | 14.4
R-410A | < -130°C | 109 | 35.4 | 8.63 | 4.45 | 7.78 | 15.8 | 1.01 | 2.76 | 9.91
R-448A | < -132°C | 60.3 | 17.8 | 3.75 | 5.25 | 9.68 | 21.1 | 1.73 | 5.22 | 21.6
R-449A | < -132°C | 60.6 | 18 | 3.82 | 5.2 | 9.56 | 20.7 | 1.73 | 5.18 | 21.2
R-454B | < -141°C | 98.8 | 32.3 | 7.85 | 4.53 | 7.94 | 16.1 | 1.09 | 2.99 | 10.7
R-717 | -77.7°C | 40.8 | 10.9 | 1.66 | 5.75 | 11.1 | 28.5 | 2.09 | 7 | 40.4
1Freezing point is determined at standard atmospheric pressure (101.325 kPa).

## Ch 48 Table 2
I-P
Table 2 Properties of Refrigerant 508B
Composition percentage by mass | R-23, 46%
R-116, 54%
ASHRAE 34 safety group | A1
Exposure limit (8h and 12h)1 | 1000 ppm
Boiling point (1 atm) | -125.7°F
Critical temperature | 52.2°F
Critical pressure | 546.9 psia
Latent heat of vaporaization at boiling point | 71.1 Btu/lb
1The exposure limit is a calculated limit determined from the Chemours airborne exposure limit (AEL) of the individual components.
The AEL is the maximum amount to which nearly all workers can be repeatedly exposed during a working lifetime without adverse effects.
SI
Table 2 Properties of Refrigerant 508B
Composition percentage by mass | R-23, 46%
R-116, 54%
ASHRAE 34 safety group | A1
Exposure limit (8h and 12h)1 | 1000 ppm
Boiling point (101.325 kPa) | -87.6°C
Critical temperature | 11.2°C
Critical pressure | 3771 kPa
Latent heat of vaporaization at boiling point | 165.4 kJ/kg
1The exposure limit is a calculated limit determined from the Chemours airborne exposure limit (AEL) of the individual components.
The AEL is the maximum amount to which nearly all workers can be repeatedly exposed during a working lifetime without adverse effects.

## Ch 48 Table 3
I-P
Table 3 Theoretical Performance of Cascade System using R-23, R-170 (Ethane), R-508B and R-1150 (Ethylene)
| R-508B | R-23 | R-170 | R-1150
Capacity (R-508B = 100) | 100 | 88.2 | 109 | 209
Efficiency (R-508B = 100) | 100 | 104 | 106 | 99.2
Discharge pressure, psia | 149 | 125 | 135 | 248
Suction pressure, psia | 17.2 | 12.7 | 18.3 | 40.4
Discharge temperature, °F | 160 | 286 | 228 | 257
Note: Operating conditions: -120°F evaporator temperature, -30°F condensing temperature,
10°F subcooling, -100°F suction temperature, compression at 70 percent isentropic efficiency.
SI
Table 3 Theoretical Performance of Cascade System using R-23, R-170 (Ethane), R-508B and R-1150 (Ethylene)
| R-508B | R-23 | R-170 | R-1150
Capacity (R-508B = 100) | 100 | 88.1 | 109 | 211
Efficiency (R-508B = 100) | 100 | 104 | 106 | 99.3
Discharge pressure, kPa | 1011 | 847 | 913 | 1682
Suction pressure, kPa | 115 | 85 | 122 | 271
Discharge temperature, °C | 70 | 140 | 108 | 123
Note: Operating conditions: -85°C evaporator temperature, -35°C condensing temperature,
5 K subcooling, -75°C suction temperature, compression at 70 percent isentropic efficiency.

## Chapter 48 Table 4
I-P
Table 4 Theoretical Compressor Performance Data for Two Different Evaporating Temperatures
Evaporating |  |  | Discharge | Volumetric
Temperature, |  | Pressure | Temperature, | Flow
°F | Refrigerant | Ratio | °F | CFM per ton
-110 | R-508B | 6.41 | 135 | 6.88
| R-23 | 7.14 | 243 | 7.76
| R-170 | 5.59 | 196 | 6.53
| R-1150 | 4.78 | 219 | 3.49
-150 | R-508B | 25.1 | 250 | 27.1
| R-23 | 29.7 | 435 | 31.1
| R-170 | 19 | 339 | 21.8
| R-1150 | 14.5 | 384 | 10.4
Note: Operating conditions: -30°F condensing temperature, 10°F subcooling,
20°F suction superheat, compression at 70 percent isentropic efficiency.
SI
Table 4 Theoretical Compressor Performance Data for Two Different Evaporating Temperatures
Evaporating |  |  | Discharge | Volumetric
Temperature, |  | Pressure | Temperature, | Flow
°C | Refrigerant | Ratio | °C | L/s per kW
-80 | R-508B | 6.68 | 57.3 | 0.97
| R-23 | 7.45 | 118 | 1.1
| R-170 | 5.8 | 91.3 | 0.92
| R-1150 | 4.94 | 108 | 0.49
-100 | R-508B | 22.7 | 114 | 3.34
| R-23 | 26.8 | 214 | 3.83
| R-170 | 17.5 | 163 | 2.72
| R-1150 | 13.4 | 187 | 1.3
Note: Operating conditions: -35°C condensing temperature, 5 K subcooling,
10°C suction superheat, compression at 70 percent isentropic efficiency.